## GC2115 CAN
Sr No. | J1939 PGN |  | SPN |  | Bit map
| PGN | Name | Name | SPN |  | Source ECU | Update Rate (msec) | STARTING BIT | LENGTH | FACTOR | OFFSET | OPERATING RANGE | Unit
1 | 64911 | Generator Total AC Percent Power | Generator Total Percent kW | 3590 | As per J1939 | GCU | 250 ms | 1-2 | 16 | 0.0078125 %/bit | -251 % | -251 to 250.99 % | %
2 | 65008 | Mains Phase B AC Basic Quantities | Mains Phase BR Line-Line AC RMS Voltage | 2477 | As per J1939 | GCU | 100 ms | 1-2 | 16 | 1 V/bit | 0 | 0 to 64,255 V | V
|  |  | Mains Phase B Line-Neutral AC RMS Voltage | 2481 | As per J1939 | GCU | 100 ms | 3-4 | 16 | 1 V/bit | 0 | 0 to 64,255 V | V
|  |  | Mains Phase B AC Frequency | 2473 | As per J1939 | GCU | 100 ms | 5-6 | 16 | 1/128 Hz/bit | 0 | 0 to 501.9921875 Hz | Hz
3 | 65011 | Mains Phase Y AC Basic Quantities | Mains Phase YB Line-Line AC RMS Voltage | 2476 | As per J1939 | GCU | 100 ms | 1-2 | 16 | 1 V/bit | 0 | 0 to 64,255 V | V
|  |  | Mains Phase Y Line-Neutral AC RMS Voltage | 2480 | As per J1939 | GCU | 100 ms | 3-4 | 16 | 1 V/bit | 0 | 0 to 64,255 V | V
|  |  | Mains Phase Y AC Frequency | 2472 | As per J1939 | GCU | 100 ms | 5-6 | 16 | 1/128 Hz/bit | 0 | 0 to 501.9921875 Hz | Hz
4 | 65014 | Mains Phase R Basic AC Quantities | Mains Phase RY Line-Line AC RMS Voltage | 2475 | As per J1939 | GCU | 100 ms | 1-2 | 16 | 1 V/bit | 0 | 0 to 64,255 V | V
|  |  | Mains Phase R Line-Neutral AC RMS Voltage | 2479 | As per J1939 | GCU | 100 ms | 3-4 | 16 | 1 V/bit | 0 | 0 to 64,255 V | V
|  |  | Mains Phase R AC Frequency | 2471 | As per J1939 | GCU | 100 ms | 5-6 | 16 | 1/128 Hz/bit | 0 | 0 to 501.9921875 Hz | Hz
5 | 65018 | Genset total RB energy | Generator total kW hours | 2468 | As per J1939 | GCU | 100 ms | 1-4 | 32 | 1 kWh/bit | 0 | 0 to 4211081215 kWh | kWh
6 | 65019 | Generator Phase B AC Reactive Power | Generator Phase B Reactive Power | 2459 | As per J1939 | GCU | 100 ms | 1-4 | 32 | 1 VAr/bit | -2,000,000,000 VAr | -2,000,000,000 to 2,211,081,215 VAr | VAr
|  |  | Generator Phase B Power Factor | 2467 | As per J1939 | GCU | 100 ms | 5-6 | 16 | 1/16384 per bit | -1 | -1.00000 to 2.921814 | 0
7 | 65020 | Generator Phase B AC Power | Generator Phase B Real Power | 2455 | As per J1939 | GCU | 100 ms | 1-4 | 32 | 1 W/bit | -2,000,000,000 Watts | -2,000,000,000 to 2,211,081,215 Watts | W
|  |  | Generator Phase B Apparent Power | 2463 | As per J1939 | GCU | 100 ms | 5-8 | 32 | 1 VA/bit | -2,000,000,000 VA | -2,000,000,000 to 2,211,081,215 VA | VA
8 | 65021 | Generator Phase B Basic AC Quantities | Generator Phase BR Line-Line AC RMS Voltage | 2443 | As per J1939 | GCU | 100 ms | 1-2 | 16 | 1 V/bit | 0 | 0 to 64,255 V | V
|  |  | Generator Phase B Line-Neutral AC RMS Voltage | 2447 | As per J1939 | GCU | 100 ms | 3-4 | 16 | 1 V/bit | 0 | 0 to 64,255 V | V
|  |  | Generator Phase B AC Frequency | 2439 | As per J1939 | GCU | 100 ms | 5-6 | 16 | 1/128 Hz/bit | 0 | 0 to 501.9921875 Hz | Hz
|  |  | Generator Phase B AC RMS Current | 2451 | As per J1939 | GCU | 100 ms | 7-8 | 16 | 1 A/bit | 0 | 0 to 64,255 A | A
9 | 65022 | Generator Phase Y AC Reactive Power | Generator Phase Y Reactive Power | 2458 | As per J1939 | GCU | 100 ms | 1-4 | 32 | 1 VAr/bit | -2,000,000,000 VAr | -2,000,000,000 to 2,211,081,215 VAr | VAr
|  |  | Generator Phase Y Power Factor | 2466 | As per J1939 | GCU | 100 ms | 5-6 | 16 | 1/16384 per bit | -1 | -1.00000 to 2.921814 | 0
10 | 65023 | Generator Phase Y AC Power | Generator Phase Y Real Power | 2454 | As per J1939 | GCU | 100 ms | 1-4 | 32 | 1 W/bit | -2,000,000,000 Watts | -2,000,000,000 to 2,211,081,215 Watts | W
|  |  | Generator Phase Y Apparent Power | 2462 | As per J1939 | GCU | 100 ms | 5-8 | 32 | 1 VA/bit | -2,000,000,000 VA | -2,000,000,000 to 2,211,081,215 VA | VA
11 | 65024 | Generator Phase Y Basic AC Quantities | Generator Phase YB Line-Line AC RMS Voltage | 2442 | As per J1939 | GCU | 100 ms | 1-2 | 16 | 1 V/bit | 0 | 0 to 64,255 V | V
|  |  | Generator Phase Y Line-Neutral AC RMS Voltage | 2446 | As per J1939 | GCU | 100 ms | 3-4 | 16 | 1 V/bit | 0 | 0 to 64,255 V | V
|  |  | Generator Phase Y AC Frequency | 2438 | As per J1939 | GCU | 100 ms | 5-6 | 16 | 1/128 Hz/bit | 0 | 0 to 501.9921875 Hz | Hz
|  |  | Generator Phase Y AC RMS Current | 2450 | As per J1939 | GCU | 100 ms | 7-8 | 16 | 1 A/bit | 0 | 0 to 64,255 A | A
12 | 65025 | Generator Phase R AC Reactive Power | Generator Phase R Reactive Power | 2457 | As per J1939 | GCU | 100 ms | 1-4 | 32 | 1 VAr/bit | -2,000,000,000 VAr | -2,000,000,000 to 2,211,081,215 VAr | VAr
|  |  | Generator Phase R Power Factor | 2465 | As per J1939 | GCU | 100 ms | 5-6 | 16 | 1/16384 per bit | -1 | -1.00000 to 2.921814 | 0
13 | 65026 | Generator Phase R AC Power | Generator Phase R Real Power | 2453 | As per J1939 | GCU | 100 ms | 1-4 | 32 | 1 W/bit | -2,000,000,000 Watts | -2,000,000,000 to 2,211,081,215 Watts | W
|  |  | Generator Phase R Apparent Power | 2461 | As per J1939 | GCU | 100 ms | 5-8 | 32 | 1 VA/bit | -2,000,000,000 VA | -2,000,000,000 to 2,211,081,215 VA | VA
14 | 65027 | Generator Phase R Basic AC Quantities | Generator Phase RY Line-Line AC RMS Voltage | 2441 | As per J1939 | GCU | 100 ms | 1-2 | 16 | 1 V/bit | 0 | 0 to 64,255 V | V
|  |  | Generator Phase R Line-Neutral AC RMS Voltage | 2445 | As per J1939 | GCU | 100 ms | 3-4 | 16 | 1 V/bit | 0 | 0 to 64,255 V | V
|  |  | Generator Phase R AC Frequency | 2437 | As per J1939 | GCU | 100 ms | 5-6 | 16 | 1/128 Hz/bit | 0 | 0 to 501.9921875 Hz | Hz
|  |  | Generator Phase R AC RMS Current | 2449 | As per J1939 | GCU | 100 ms | 7-8 | 16 | 1 A/bit | 0 | 0 to 64,255 A | A
15 | 65028 | Generator Total AC Reactive Power | Generator Total Reactive Power | 2456 | As per J1939 | GCU | 100 ms | 1-4 | 32 | 1 VAr/bit | -2,000,000,000 VAr | -2,000,000,000 to 2,211,081,215 VAr | VAr
|  |  | Generator Overall Power Factor | 2464 | As per J1939 | GCU | 100 ms | 5-6 | 16 | 1/16384 per bit | -1 | -1.00000 to 2.921814 | 0
16 | 65029 | Generator Total AC Power | Generator Total Real Power | 2452 | As per J1939 | GCU | 100 ms | 1-4 | 32 | 1 W/bit | -2,000,000,000 Watts | -2,000,000,000 to 2,211,081,215 Watts | W
|  |  | Generator Total Apparent Power | 2460 | As per J1939 | GCU | 100 ms | 5-8 | 32 | 1 VA/bit | -2,000,000,000 VA | -2,000,000,000 to 2,211,081,215 VA | VA
17 | 65030 | Generator Average Basic AC Quantities | Generator Average Line-Line AC RMS Voltage | 2440 | As per J1939 | GCU | 100 ms | 1-2 | 16 | 1 V/bit | 0 | 0 to 64,255 V | V
|  |  | Generator Average Line-Neutral AC RMS Voltage | 2444 | As per J1939 | GCU | 100 ms | 3-4 | 16 | 1 V/bit | 0 | 0 to 64,255 V | V
|  |  | Generator Average AC Frequency | 2436 | As per J1939 | GCU | 100 ms | 5-6 | 16 | 1/128 Hz/bit | 0 | 0 to 501.9921875 Hz | Hz
|  |  | Generator Average AC RMS Current | 2448 | As per J1939 | GCU | 100 ms | 7-8 | 16 | 1 A/bit | 0 | 0 to 64,255 A | A
Sr No. | PGN | Description | SPN Description | Byte mapping | Bit map | Source ECU | Update Rate (msec) | STARTING BIT | LENGTH | FACTOR | OFFSET | OPERATING RANGE | Unit
18 | 65280 | SEDEMAC_Prop_B_2 | Sedemac mode: SEDEMAC Mode | Byte 0 | 0-1 bits (0- Manual engine off 1- Auto mode 2-Manual engine on 3-Other than above mode (Config Mode) ) | GCU | 1000 ms | 1.1 | 2 bit | 1 | 0 | 0-1 bits (0- Manual engine off 1- Auto mode 2-Manual engine on 3-Other than above mode (Config Mode) )
|  |  | Reserved |  | 2-7 bits | GCU | 1000 ms | 1.3 | 6 bit | 1 | 0
|  |  | Digital input J | Byte 2 | 15 | GCU | 500 ms | 3.8 | 1 bit | 1 | 0
|  |  | Digital input K |  | 14 | GCU | 500 ms | 3.7 | 1 bit | 1 | 0
|  |  | Digital input L |  | 13 | GCU | 500 ms | 3.6 | 1 bit | 1 | 0
|  |  | Digital input M |  | 12 | GCU | 500 ms | 3.5 | 1 bit | 1 | 0
|  |  | Digital input N |  | 11 | GCU | 500 ms | 3.4 | 1 bit | 1 | 0
|  |  | Digital input O |  | 10 | GCU | 500 ms | 3.3 | 1 bit | 1 | 0
|  |  | Digital input P |  | 9 | GCU | 500 ms | 3.2 | 1 bit | 1 | 0
|  |  | Digital Output P |  | 8 | GCU | 500 ms | 3.1 | 1 bit | 1 | 0
|  |  | Digital output H | Byte 1 | 7 | GCU | 500 ms | 2.8 | 1 bit | 1 | 0
|  |  | Digital output I |  | 6 | GCU | 500 ms | 2.7 | 1 bit | 1 | 0
|  |  | Digital Output J |  | 5 | GCU | 500 ms | 2.6 | 1 bit | 1 | 0
|  |  | Digital Output K |  | 4 | GCU | 500 ms | 2.5 | 1 bit | 1 | 0
|  |  | Digital Output L |  | 3 | GCU | 500 ms | 2.4 | 1 bit | 1 | 0
|  |  | Digital Output M |  | 2 | GCU | 500 ms | 2.3 | 1 bit | 1 | 0
|  |  | Digital Output N |  | 1 | GCU | 500 ms | 2.2 | 1 bit | 1 | 0
|  |  | Digital Output O |  | 0 | GCU | 500 ms | 2.1 | 1 bit | 1 | 0
|  |  | Min healthy frequency | Byte 3 | Byte 3 | GCU | 1000 ms | 4 | 8 | 1 | 0
|  |  | Min healthy voltage | Byte 4-5 | Byte 4-5 | GCU | 1000 ms | 5-6 | 16 | 1 | 0
|  |  | Reserved | Byte 6-7 | Byte 6-7 | GCU | 1000 ms | 7-8 | 16 | 1 | 0
19 | 65289 | Prop Bit Fields 1 | Digital input a | 8-15 byte 1 | 15 | GCU | 500 ms | 2.8 | 1 bit | 1 | 0
|  |  | Digital input b |  | 14 | GCU | 500 ms | 2.7 | 1 bit | 1 | 0
|  |  | Digital input c |  | 13 | GCU | 500 ms | 2.6 | 1 bit | 1 | 0
|  |  | Digital input d |  | 12 | GCU | 500 ms | 2.5 | 1 bit | 1 | 0
|  |  | Digital input e |  | 11 | GCU | 500 ms | 2.4 | 1 bit | 1 | 0
|  |  | Digital input f |  | 10 | GCU | 500 ms | 2.3 | 1 bit | 1 | 0
|  |  | Digital input g |  | 9 | GCU | 500 ms | 2.2 | 1 bit | 1 | 0
|  |  | Digital input h |  | 8 | GCU | 500 ms | 2.1 | 1 bit | 1 | 0
|  |  | Digital input i | 0-7 byte 0 | 7 | GCU | 500 ms | 1.8 | 1 bit | 1 | 0
|  |  | Digital output a |  | 6 | GCU | 500 ms | 1.7 | 1 bit | 1 | 0
|  |  | Digital output b |  | 5 | GCU | 500 ms | 1.6 | 1 bit | 1 | 0
|  |  | Digital output c |  | 4 | GCU | 500 ms | 1.5 | 1 bit | 1 | 0
|  |  | Digital output d |  | 3 | GCU | 500 ms | 1.4 | 1 bit | 1 | 0
|  |  | Digital output e |  | 2 | GCU | 500 ms | 1.3 | 1 bit | 1 | 0
|  |  | Digital output f |  | 1 | GCU | 500 ms | 1.2 | 1 bit | 1 | 0
|  |  | Digital output g |  | 0 | GCU | 500 ms | 1.1 | 1 bit | 1 | 0
|  |  | GCU Mode | Byte 3 | 31(Config Mode 1/In Other Mode-0) | GCU | 500 ms | 4.8 | 1 bit | 1 | 0
|  |  | Mains Healthy / unhealthy |  | 30 (healthy 0 / unhealthy 1) | GCU | 500 ms | 4.7 | 1 bit | 1 | 0 | 30 (healthy 0 / unhealthy 1)
|  |  | Genset operation mode |  | 27-29(Auto- 101 Manual-100 Reserved) | GCU | 500 ms | 4.4-4.6 | 3 bit | 1 | 0 | 27-29(Auto- 101 Manual-100 Reserved)
|  |  | Load on Mains |  | 26 | GCU | 500 ms | 4.3 | 1 bit | 1 | 0
|  |  | Load on Genset |  | 25 | GCU | 500 ms | 4.2 | 1 bit | 1 | 0
|  |  | Current Genset status |  | 24(0- Stopped 1- Running ) | GCU | 500 ms | 4.1 | 1 bit | 1 | 0 | 24(0- Stopped 1- Running )
|  |  | Genset stopped normally | Byte 2 | 23 | GCU | 500 ms | 3.8 | 1 bit | 1 | 0
|  |  | Genset in fault |  | 22 | GCU | 500 ms | 3.7 | 1 bit | 1 | 0
|  |  | Genset fail to start |  | 21 | GCU | 500 ms | 3.6 | 1 bit | 1 | 0
|  |  | Gen available |  | 20 | GCU | 500 ms | 3.5 | 1 bit | 1 | 0
|  |  | Common shut down |  | 19 | GCU | 500 ms | 3.4 | 1 bit | 1 | 0
|  |  | Common electric trip |  | 18 | GCU | 500 ms | 3.3 | 1 bit | 1 | 0
|  |  | Common warning |  | 17 | GCU | 500 ms | 3.2 | 1 bit | 1 | 0
|  |  | Common notification |  | 16 | GCU | 500 ms | 3.1 | 1 bit | 1 | 0
|  |  | No of starts | 4-5 Byte | 4-5 Byte | GCU | 500 ms | 5-6 | 16 | 1 | 0
|  |  | No of trips | 6-7 Byte | 6-7 Byte | GCU | 500 ms | 7-8 | 16 | 1 | 0
20 | 65290 | Run Hours | Eng run hrs | 0-1 Byte | 2 Bytes | GCU | 500 ms | 1-2 | 16 | 1 | 0
|  |  | Eng run min | 2-3 Byte | 2 Bytes | GCU | 500 ms | 3-4 | 16 | 1 | 0
|  |  | EGR Inducement Timer | 4-7 Byte | 2 Bytes | GCU | 500 ms | 5-8 | 32 | 1 | 0
|  |  | EGR Heal Timer |  | 2 Bytes | GCU | 500 ms | 5-8 | 32 | 1 | 0
21 | 65291 | Alarms registers 1 to 4 | Low oil pressure | 0-1 Byte | 12-15 | GCU | 500 ms | 2.5-2.8 | 4 bit | 1 | 0
|  |  | High coolant temperature |  | 8-11 | GCU | 500 ms | 2.1-2.4 | 4 bit | 1 | 0
|  |  | Low fuel level |  | 4-7 | GCU | 500 ms | 1.5-1.8 | 4 bit | 1 | 0
|  |  | Water level switch |  | 0-3 | GCU | 500 ms | 1.1-1.4 | 4 bit | 1 | 0
|  |  | Under speed | 2-3 Byte | 28-31 | GCU | 500 ms | 4.5-4.8 | 4 bit | 1 | 0
|  |  | Over speed |  | 24-27 | GCU | 500 ms | 4.1-4.4 | 4 bit | 1 | 0
|  |  | Fail to start |  | 20-23 | GCU | 500 ms | 3.5-3.8 | 4 bit | 1 | 0
|  |  | Fail to stop |  | 16-19 | GCU | 500 ms | 3.1-3.4 | 4 bit | 1 | 0
|  |  | Reserved | 4-5 Byte | 40-43 | GCU | 500 ms | 6.1-6.4 | 4 bit | 1 | 0
|  |  | Reserved 1 |  | 44-47 | GCU | 500 ms | 6.5-6.8 | 4 bit | 1 | 0
|  |  | Generator low frequency |  | 36-39 | GCU | 500 ms | 5.5-5.8 | 4 bit | 1 | 0
|  |  | Generator high frequency |  | 32-35 | GCU | 500 ms | 5.1-5.4 | 4 bit | 1 | 0
|  |  | Generator high current | 6-7 Byte | 60-63 | GCU | 500 ms | 8.5-8.8 | 4 bit | 1 | 0
|  |  | Generator overload |  | 56-59 | GCU | 500 ms | 8.1-8.4 | 4 bit | 1 | 0
|  |  | Unbalanced load |  | 52-55 | GCU | 500 ms | 7.5-7.8 | 4 bit | 1 | 0
|  |  | Emergency stop |  | 48-51 | GCU | 500 ms | 7.1-7.4 | 4 bit | 1 | 0
22 | 65292 | Alarm registers 5 to 8 | Reserved 1 | 0-1 Byte | 4-7 | GCU | 500 ms | 1.5-1.8 | 4 bit | 1 | 0
|  |  | Maintenance |  | 8-11 | GCU | 500 ms | 2.1-2.4 | 4 bit | 1 | 0
|  |  | Charge alternator failure |  | 12-15 | GCU | 500 ms | 2.5-2.8 | 4 bit | 1 | 0
|  |  | Reserved |  | 0-3 | GCU | 500 ms | 1.1-1.4 | 4 bit | 1 | 0
|  |  | Battery low voltage | 2-3 Byte | 28-31 | GCU | 500 ms | 4.5-4.8 | 4 bit | 1 | 0
|  |  | Battery high voltage |  | 24-27 | GCU | 500 ms | 4.1-4.4 | 4 bit | 1 | 0
|  |  | Temperature Circuit open |  | 20-23 | GCU | 500 ms | 3.5-3.8 | 4 bit | 1 | 0
|  |  | Reserved |  | 16-19 | GCU | 500 ms | 3.1-3.4 | 4 bit | 1 | 0
|  |  | Fuel theft | 4-5 Byte | 44-47 | GCU | 500 ms | 6.5-6.8 | 4 bit | 1 | 0
|  |  | MPU lost |  | 40-43 | GCU | 500 ms | 6.1-6.4 | 4 bit | 1 | 0
|  |  | Oil pressure Open circuit |  | 36-39 | GCU | 500 ms | 5.5-5.8 | 4 bit | 1 | 0
|  |  | Auxiliary input i |  | 32-35 | GCU | 500 ms | 5.1-5.4 | 4 bit | 1 | 0
|  |  | Auxiliary input a | 6-7 Byte | 60-63 | GCU | 500 ms | 8.5-8.8 | 4 bit | 1 | 0
|  |  | Auxiliary input b |  | 56-59 | GCU | 500 ms | 8.1-8.4 | 4 bit | 1 | 0
|  |  | Auxiliary input c |  | 52-55 | GCU | 500 ms | 7.5-7.8 | 4 bit | 1 | 0
|  |  | Auxiliary input d |  | 48-51 | GCU | 500 ms | 7.1-7.4 | 4 bit | 1 | 0
23 | 65293 | Alarm registers 9 to 12 | Auxiliary input e | 0-1 Byte | 12-15 | GCU | 500 ms | 2.5-2.8 | 4 bit | 1 | 0
|  |  | Auxiliary input f |  | 8-11 | GCU | 500 ms | 2.1-2.4 | 4 bit | 1 | 0
|  |  | Auxiliary input g |  | 4-7 | GCU | 500 ms | 1.5-1.8 | 4 bit | 1 | 0
|  |  | Auxiliary input h |  | 0-3 | GCU | 500 ms | 1.1-1.4 | 4 bit | 1 | 0
|  |  | Gen L1 phase low volt | 2-3 Byte | 28-31 | GCU | 500 ms | 4.5-4.8 | 4 bit | 1 | 0
|  |  | Gen L1 phase high volt |  | 24-27 | GCU | 500 ms | 4.1-4.4 | 4 bit | 1 | 0
|  |  | Gen L2 phase low volt |  | 20-23 | GCU | 500 ms | 3.5-3.8 | 4 bit | 1 | 0
|  |  | Gen L2 phase high volt |  | 16-19 | GCU | 500 ms | 3.1-3.4 | 4 bit | 1 | 0
|  |  | Gen L3 phase low volt | 4-5 Byte | 44-47 | GCU | 500 ms | 6.5-6.8 | 4 bit | 1 | 0
|  |  | Gen L3 phase high volt |  | 40-43 | GCU | 500 ms | 6.1-6.4 | 4 bit | 1 | 0
|  |  | Genset phase rotation |  | 36-39 | GCU | 500 ms | 5.5-5.8 | 4 bit | 1 | 0
|  |  | Mains phase rotation |  | 32-35 | GCU | 500 ms | 5.1-5.4 | 4 bit | 1 | 0
|  |  | Fuel level Open Circuit | 6-7 Byte | 60-63 | GCU | 500 ms | 8.5-8.8 | 4 bit | 1 | 0
|  |  | Reserved |  | 56-59 | GCU | 500 ms | 8.1-8.4 | 4 bit | 1 | 0
|  |  | Reserved |  | 52-55 | GCU | 500 ms | 7.5-7.8 | 4 bit | 1 | 0
|  |  | High oil pressure detected |  | 48-51 | GCU | 500 ms | 7.1-7.4 | 4 bit | 1 | 0
24 | 65294 | Alarm registers 13 to 16 | Auxailiary input J | 0-1 Byte | 12-15 | GCU | 500 ms | 2.5-2.8 | 4 bit | 1 | 0
|  |  | Auxailiary input K |  | 8-11 | GCU | 500 ms | 2.1-2.4 | 4 bit | 1 | 0
|  |  | Auxailiary input L |  | 4-7 | GCU | 500 ms | 1.5-1.8 | 4 bit | 1 | 0
|  |  | Auxailiary input M |  | 0-3 | GCU | 500 ms | 1.1-1.4 | 4 bit | 1 | 0
|  |  | Auxailiary input N | 2-3 Byte | 28-31 | GCU | 500 ms | 4.5-4.8 | 4 bit | 1 | 0
|  |  | Auxailiary input O |  | 24-27 | GCU | 500 ms | 4.1-4.4 | 4 bit | 1 | 0
|  |  | Auxailiary input P |  | 20-23 | GCU | 500 ms | 3.5-3.8 | 4 bit | 1 | 0
|  |  | Reserved |  | 16-19 | GCU | 500 ms | 3.1-3.4 | 4 bit | 1 | 0
|  |  | Reserved | 4-5 Byte | 44-47 | GCU | 500 ms | 6.5-6.8 | 4 bit | 1 | 0
|  |  | Reserved |  | 40-43 | GCU | 500 ms | 6.1-6.4 | 4 bit | 1 | 0
|  |  | Reserved |  | 36-39 | GCU | 500 ms | 5.5-5.8 | 4 bit | 1 | 0
|  |  | Reserved |  | 32-35 | GCU | 500 ms | 5.1-5.4 | 4 bit | 1 | 0
|  |  | Reserved | 6-7 Byte | 60-63 | GCU | 500 ms | 8.5-8.8 | 4 bit | 1 | 0
|  |  | Reserved |  | 56-59 | GCU | 500 ms | 8.1-8.4 | 4 bit | 1 | 0
|  |  | Reserved |  | 52-55 | GCU | 500 ms | 7.5-7.8 | 4 bit | 1 | 0
|  |  | Reserved |  | 48-51 | GCU | 500 ms | 7.1-7.4 | 4 bit | 1 | 0
25 | 65295 | Fuel level and Lube Oil pressure | Genset Rating | 6-7 Byte | 6-7 Byte | GCU | 500 ms | 7-8 | 16 | 1 | 0
|  |  | Fuel in liters | 4-5 Byte | 4-5 Byte | GCU | 500 ms | 5-6 | 16 | 1 | 0
|  |  | Reserved | 2-3 byte | 2-3 byte | GCU | 500 ms | 3-4 | 16 | 1 | 0
|  |  | LOP pressure | 0-1 Byte | 0-1 Byte | GCU | 500 ms | 1-2 | 16 | 1 | 0
26 | 65296 | Genset Cumulative Kwh and KVAh | Generator Cumulative KWh | 0-3 Byte | 0-3 Byte | GCU | 500 ms | 1-4 | 32 | 1 | 0
|  |  | Generator Cumulative KVAh | 4-7 Byte | 4-7 Byte | GCU | 500 ms | 5-8 | 32 | 1 | 0
27 | 65297 | Genset Cumulative KVArh | Generator Cumulative KVArh | 0-3 Byte | 0-3 Byte | GCU | 500 ms | 1-4 | 32 | 1 | 0
|  |  | Reserved | 4-7 Byte | 4-7 Byte | GCU | 500 ms | 5-8 | 32 | 1 | 0
SR# | PGN | Message Name | Parameter Description |  | SPN | Source ECU | Update Rate (msec) | STARTING BIT | LENGTH | FACTOR | OFFSET | OPERATING RANGE | Unit
1 | 61444 | EEC1 | Engine Speed |  | 190 | Engine | 10 | 4.1 | 16 | 0.125 | 0 | 0/8191.875 | rpm
2 | 65262 | ET1 | Engine Coolant Temperature |  | 110 | Engine | 1000 | 1.1 | 8 | 1 | -40 | -0.18605 | deg C
3 | 65262 | ET1 | Engine Oil Temperature 1 |  | 175 | Engine | 1000 | 3.1 | 16 | 0.03125 | -273 | -273 to 1734.96875 °C | deg C
4 | 65263 | EFL/P1 | Engine Oil Pressure |  | 100 | Engine | 500 | 4.1 | 8 | 4 | 0 | 0/1020 | kPa
5 | 61444 | EEC1 | Actual Engine - Percent Torque |  | 513 | Engine | 10 | 3.1 | 8 | 1 | -125 | -0.96154 | %
6 | 61475 | A1SCRDSI1 | Aftertreatment 1 SCR Actual Dosing Reagent Quantity |  | 4331 | Engine | 50 | 1.1 | 16 | 0.0313 | 0 | 0/2051.2455 | g/hr
7 | 64800 | A1DOC1 | Aftertreatment 1 Diesel Particulate Filter Intake Temperature |  | 4766 | Engine | 500 | 3.1 | 16 | 0.0313 | -273 | -0.15352 | deg C
8 | 65110 | TI /AT1T1I1 | Catalyst Tank Level |  | 1761 | Engine | 1000 | 1.1 | 8 | 0.4 | 0 | 0/102 | %
9 | 65110 | TI /AT1T1I1 | Aftertreatment SCR Operator Inducement Severity |  | 5246 | Engine | 1000 | 6.6 | 3 | 1 | 0 | 0/7 | State
10 | 65253 | HOURS | Total Engine Hours of Operation |  | 247 | Engine | On request | 1.1 | 32 | 0.05 | 0 | 0/214748364.75 | hr
11 | 64923 | A1DEFI1 | Aftertreatment 1 Diesel Exhaust Fluid Concentration |  | 3516 | Engine | 1000 | 2.1 | 8 | 0.25 | 0 | 0 to 62.5 % | %
12 | 65110 | TI /AT1T1I1 | Low Adblue Level Warning |  | 5245 | Engine | 1000 | 5.6 | 3 | 1 | 0 | 0/7 | State
13 | 64554 | OII | Operator Inducement Time to Final Inducement Action |  | 7719 | Engine | 10000 | 7.1 | 16 | 1 | 0 | 0 to 64,255 | min
14 | 65279 | OI | Water In Fuel Indicator 1 |  | 97 | Engine | 10000 | 1.1 | 2 | 1 | 0 | 0 to 3 | bit
15 | 65266 | LFE1 | Engine Fuel Rate |  | 183 | Engine | 100 | 1.1 | 16 | 0.05 | 0 | 0 to 3,212.75 | l/h
16 | 65257 | LFC | Engine Total Fuel Used |  | 250 | Engine | On request | 5.1 | 32 | 0.5 | 0 | 0/2147483647.5 | L
17 | 65247 | EEC3 | Aftertreatment 1 Exhaust Gas Mass Flow Rate |  | 3236 | Engine | 250 | 6.1 | 16 | 0.2 | 0 | 0/13107 | kg/h
18 | 64830 | A1SCREGT1 | Aftertreatment 1 SCR Exhaust Gas Temperature 1 |  | 4360 | Engine | 500 | 1.1 | 16 | 0.03125 | -273 °C | -273 to 1734.96875 °C | deg C