## Modbus (For Internal Usage) (hidden)
Note: THIS SHEET IS CONFIDENTIAL. USB PROTOCOL DETAILS NOT TO BE SHARED WITH CUSTOMER. ADDITIONALLY SOME FIELDS ON MODBUS ARE PROCOM SPECIFIC.
Note: Modbus specification mostly defined by Indus with some additional fields added by Procom
Sn. | Parameters | Units of | Data Type | Size in byte | Conversion | Type of Register | Modbus | No. of | Remarks
|  | Measurement | (Float/Hex etc.) |  | Multiplier to read the data |  | Register Address | Registers required
INPUT REGISTER
1 | Product Type (Nextgen Generator - 20) | NA | Unsigned Integer | 2 | 1 | Input Register | 1 | 1 | 20->NextGen Generator
2 | Product Make ( M&M-110) | NA | Unsigned Integer | 2 | 1 | Input Register | 2 | 1 | 100->TMTL 110->M&M 0->Procom
3 | Generator Phase (1 for Single Phase 3 for Three Phase) | NA | Unsigned Integer | 2 | 1 | Input Register | 3 | 1
4 | Fuel Type (Diesel -1 , Gas-2) | NA | Unsigned Integer | 2 | 1 | Input Register | 4 | 1 | 1->Diesel
5 | Product Rating (Please mention the exact rating) | NA | Unsigned Long Integer | 4 | 0.1 | Input Register | 2020-06-05 | 2 | Rating in KVA
6 | SOFTWARE/FIRMWAREVERSION (Partner Specific) | Version | Unsigned Integer | 2 | 0.01 | Input Register | 7 | 1
7 | PROTOCOLVERSION (Indus Priority) - 23 | Version | Unsigned Integer | 2 | 1 | Input Register | 8 | 1
8 | Genset Serial No | NA | ASCII String | 20 | NA | Input Register | 2018-09-01 | 10 | Max 19 characters (null-terminated)
9 | Engine Serial No | NA | ASCII String | 20 | NA | Input Register | 19-28 | 10 | Max 19 characters (null-terminated)
10 | Alternator Serial No | NA | ASCII String | 20 | NA | Input Register | 29-38 | 10 | Max 19 characters (null-terminated)
11 | Main Controller Serial No | NA | ASCII String | 20 | NA | Input Register | 40-49 | 10 | Max 19 characters (null-terminated)
12 | Engine Controller Serial No | NA | ASCII String | 20 | NA | Input Register | 50-59 | 10 | Max 19 characters (null-terminated)
13 | SITE ID | NA | ASCII String | 10 | NA | Input Register | 60-64 | 5 | Max 19 characters (null-terminated). But only the first 9 characters are shown if it's length exceeds 9 character.
14 | DATE | Date | Unsigned Integer | 2 | 1 | Input Register | 65 | 1 | Current Date
15 | HOUR | Hour | Unsigned Integer | 2 | 1 | Input Register | 66 | 1 | Current Hour
16 | MINUTES | Minutes | Unsigned Integer | 2 | 1 | Input Register | 67 | 1 | Current Minutes
17 | SECONDS | Seconds | Unsigned Integer | 2 | 1 | Input Register | 68 | 1 | Current Seconds
18 | MONTH | Month | Unsigned Integer | 2 | 1 | Input Register | 69 | 1 | Current Month
19 | YEAR | Year | Unsigned Integer | 2 | 1 | Input Register | 70 | 1 | Current Year
20 | Generator R Phase Voltage | Volt | Unsigned Integer | 2 | 0.01 | Input Register | 71 | 1
21 | Generator Y Phase Voltage | Volt | Unsigned Integer | 2 | 0.01 | Input Register | 72 | 1
22 | Generator B Phase Voltage | Volt | Unsigned Integer | 2 | 0.01 | Input Register | 73 | 1
23 | Generator Line Voltage RY | Volt | Unsigned Integer | 2 | 0.01 | Input Register | 74 | 1
24 | Generator Line Voltage YB | Volt | Unsigned Integer | 2 | 0.01 | Input Register | 75 | 1
25 | Generator Line Voltage BR | Volt | Unsigned Integer | 2 | 0.01 | Input Register | 76 | 1
26 | Generator Frequency | Hz | Unsigned Integer | 2 | 0.01 | Input Register | 77 | 1
27 | N-E (Neutral to Earth) Voltage | Volt | Unsigned Integer | 2 | 0.01 | Input Register | 78 | 1 | Always 0 (Not populated)
28 | Load Current R Phase | Amps | Unsigned Integer | 2 | 0.01 | Input Register | 79 | 1
29 | Load Current Y Phase | Amps | Unsigned Integer | 2 | 0.01 | Input Register | 80 | 1
30 | Load Current B Phase | Amps | Unsigned Integer | 2 | 0.01 | Input Register | 81 | 1
31 | Total Load Current | Amps | Unsigned Integer | 2 | 0.01 | Input Register | 82 | 1
32 | R Phase Power Factor | PF | Unsigned Integer | 2 | 0.01 | Input Register | 83 | 1
33 | Y Phase Power Factor | PF | Unsigned Integer | 2 | 0.01 | Input Register | 84 | 1
34 | B Phase Power Factor | PF | Unsigned Integer | 2 | 0.01 | Input Register | 85 | 1
35 | Engine Speed (RPM) | RPM | Unsigned Long Integer | 4 | 1 | Input Register | 86- 87 | 2
36 | Generator Total Run Hours | Hour | Unsigned Long Integer | 4 | 0.1 | Input Register | 88- 89 | 2 | Doesn't include Tamper run hours
37 | Generator Auto Run Hours | Hour | Unsigned Long Integer | 4 | 0.1 | Input Register | 90- 91 | 2 | Doesn't include Tamper run hours
38 | Generator Manual Run Hours | Hour | Unsigned Long Integer | 4 | 0.1 | Input Register | 92- 93 | 2 | Doesn't include Tamper run hours
39 | Generator No Load Run Hours | Hour | Unsigned Long Integer | 4 | 0.1 | Input Register | 94- 95 | 2 | Doesn't include Tamper run hours
40 | Generator ON Load Run Hours | Hour | Unsigned Long Integer | 4 | 0.1 | Input Register | 96-97 | 2 | Doesn't include Tamper run hours
41 | Generator Output Power - Real | KW | Unsigned Integer | 2 | 0.01 | Input Register | 98 | 1
42 | Generator Output Power - Apparent | KVA | Unsigned Integer | 2 | 0.01 | Input Register | 99 | 1
43 | Generator Output Power - Reactive | KVAR | Unsigned Integer | 2 | 0.01 | Input Register | 100 | 1
44 | Total Generator Energy | KWH | Unsigned Long Integer | 4 | 0.01 | Input Register | 101-102 | 2 | Doesn't include Tamper KWh
45 | Canopy Temperature (above Engine) | Degree C | Unsigned Integer | 2 | 0.1 | Input Register | 103 | 1 | Always 0xffff (Not populated)
46 | Canopy Temperature (far end side from Radiator) | Degree C | Unsigned Integer | 2 | 0.1 | Input Register | 104 | 1
47 | Air Inlet Temperature | Degree C | Unsigned Integer | 2 | 0.1 | Input Register | 105 | 1 | Always 0xffff (Not populated)
48 | Fuel Temperature | Degree C | Unsigned Integer | 2 | 0.1 | Input Register | 106 | 1 | Always 0xffff (Not populated)
49 | Exhaust Temperature | Degree C | Unsigned Long Integer | 4 | 0.1 | Input Register | 107-108 | 2 | Always 0xffffffff (Not populated)
50 | Catalyst Converter Temperature | Degree C | Unsigned | 4 | 0.1 | Input Register | 109-110 | 2 | Always 0xffffffff (Not populated)
51 | Engine Coolant Temp | Degree C | Unsigned Long Integer | 4 | 0.1 | Input Register | 111-112 | 2 | 0xffffffff when Sensor Open or if sensor is disabled.
52 | Radiator Coolant Temp - inlet | Degree C | Unsigned Long Integer | 4 | 0.1 | Input Register | 113-114 | 2 | Always 0xffffffff (Not populated)
53 | Radiator Coolant Temp - outlet | Degree C | Unsigned Long Integer | 4 | 0.1 | Input Register | 115-116 | 2 | Always 0xffffffff (Not populated)
54 | Stop Solenoid Body Temperature | Degree C | Unsigned Long Integer | 4 | 0.1 | Input Register | 117-118 | 2 | Always 0xffffffff (Not populated)
55 | LLOP (Low Lube oil pressure) | psi | Unsigned Integer | 2 | 0.01 | Input Register | 119 | 1 | 0xffff when Sensor Open or if sensor is disabled.
56 | Generator Battery Voltage | Volt | Unsigned Integer | 2 | 0.01 | Input Register | 120 | 1
57 | Fuel Level % | % | Unsigned Integer | 2 | 0.01 | Input Register | 121 | 1 | 0xffffffff when Sensor Open or if sensor is disabled.
58 | Fuel Consumed in liter | Liter | Unsigned Long Integer | 4 | 0.01 | Input Register | 122-123 | 2 | Always 0xffffffff (Not populated)
59 | Gas Consumed in SCM | SCM | Unsigned Long Integer | 4 | 0.01 | Input Register | 124-125 | 2 | Always 0xffffffff (Not populated)
60 | Total no of Cranks | Nos | Unsigned Long Integer | 4 | 0.01 | Input Register | 126-127 | 2
61 | No of Cranks failed attempt | Nos | Unsigned Long Integer | 4 | 0.01 | Input Register | 128-129 | 2
62 | Air Inlet Pressure | mBar | Unsigned Integer | 2 | 0.01 | Input Register | 130 | 1 | Always 0xffff (Not populated)
63 | Engine Oil Level % | % | Unsigned Integer | 2 | 0.01 | Input Register | 131 | 1 | Always 0xffff (Not populated)
64 | Turbo Oil Pressure | mBar | Unsigned Integer | 2 | 0.01 | Input Register | 132 | 1 | Always 0xffff (Not populated)
65 | Engine Coolant Level % | % | Unsigned Integer | 2 | 0.01 | Input Register | 133 | 1 | Always 0xffff (Not populated)
66 | Pilot Regulator input Pressure | mBar | Unsigned Integer | 2 | 0.01 | Input Register | 134 | 1 | Always 0xffff (Not populated)
67 | Pilot Regulator output Pressure | mBar | Unsigned Integer | 2 | 0.01 | Input Register | 135 | 1 | Always 0xffff (Not populated)
68 | Engine (Gas or Diesel) (For Diesel- 1 and Gas- 2) | NA | Unsigned Integer | 2 | 1 | Input Register | 136 | 1 | 1->Diesel
69 | DG Vibration Sensor output in kHz or Volt |  | Unsigned Integer | 2 | 0.01 | Input Register | 137 | 1 | Always 0xffff (Not populated)
70 | Radiator Water Level | % | Unsigned Integer | 2 | 0.01 | Input Register | 138 | 1 | Always 0xffff (Not populated)
71 | NTP Factor Auto Calculation | Nos | Unsigned Integer | 2 | 0.01 | Input Register | 139 | 1 | Always 0xffff (Not populated)
72 | AVR Excitation Voltage | Volt | Unsigned Integer | 2 | 0.01 | Input Register | 140 | 1 | Always 0xffff (Not populated)
73 | Lube Oil Viscosity | mm2/S | Unsigned Integer | 2 | 0.01 | Input Register | 141 | 1 | Always 0xffff (Not populated)
74 | Started on Auto mode or Manual | NA | Unsigned Integer | 2 | 1 | Input Register | 142 | 1 | 0->Manual Mode 1->Remote Mode
Mode (Automode-1,Manual Mode- 0)
75 | DG On Trigger due to Battery Volt. or Shelter Temp. (Battery - 1, temp-2) | NA | Unsigned Integer | 2 | 1 | Input Register | 143 | 1 | Always 0xffff (Not populated)
76 | Service Hours (No. of Hours since last service) | Hrs | Unsigned Integer | 4 | 0.1 | Input Register | 144 | 2 | (Not to be mentioned in catalog. For Procom's usage only.)
77 | Due Service Hours (No. of hours till next service) | Hrs | Unsigned Integer | 4 | 0.1 | Input Register | 146 | 2 | (Not to be mentioned in catalog. For Procom's usage only.)
78 | FuelInLiters | Ltrs | Unsigned Integer | 4 | 0.01 | Input Register | 148 | 2 | (Not to be mentioned in catalog. For Procom's usage only.) 0xffffffff when Sensor Open or if sensor is disabled or if tank capacity setting is disabled.
79 | FaultFlagLower | NA | Unsigned Integer | 4 | 1 | Input Register | 150 | 2 | (Not to be mentioned in catalog. For Procom's usage only.) See FAULT_XXX macros in FlagDef.h for information about this bitmask
80 | FaultFlagUpper | NA | Unsigned Integer | 4 | 1 | Input Register | 152 | 2 | (Not to be mentioned in catalog. For Procom's usage only.) See FAULT_WARN_XXX macros in FlagDef.h for information about this bitmask
81 | Comissioning Date | NA | Unsigned Integer | 2 | 1 | Input Register | 154 | 1 | (Not to be mentioned in catalog. For Procom's usage only.)
82 | Comissioning Month | NA | Unsigned Integer | 2 | 1 | Input Register | 155 | 1 | (Not to be mentioned in catalog. For Procom's usage only.)
83 | Comissioning Year | NA | Unsigned Integer | 2 | 1 | Input Register | 156 | 1 | (Not to be mentioned in catalog. For Procom's usage only.)
84 | Unix Epoch Time | NA | Unsigned Integer | 4 | 1 | Input Register | 157-158 | 2 | (Not to be mentioned in catalog. For Procom's usage only.)
85 | Tamper Run Hours | NA | Unsigned Integer | 4 | 0.1 | Input Register | 159-160 | 2 | (Not to be mentioned in catalog. For Procom's usage only.)
86 | Tamper KWh | NA | Unsigned Integer | 4 | 0.01 | Input Register | 161-162 | 2 | (Not to be mentioned in catalog. For Procom's usage only.)
87 | NCD Error Hrs | Hour | Unsigned Long Integer | 4 | 0.1 | Input Register | 163-164 | 2
88 | NCD Heal Hrs | Hour | Unsigned Long Integer | 4 | 0.1 | Input Register | 165-166 | 2
INPUT STATUS (Alarm)
1 | Fire/Smoke | NA | BIT | NA | NA | Input Status | 1 | 1
2 | Canopy Door Open | NA | BIT | NA | NA | Input Status | 2 | 1
3 | Load on Generator | NA | BIT | NA | NA | Input Status | 3 | 1
4 | Generator Fail to Start | NA | BIT | NA | NA | Input Status | 4 | 1
5 | Generator Fail to Stop | NA | BIT | NA | NA | Input Status | 5 | 1
6 | Generator Common Fault | NA | BIT | NA | NA | Input Status | 6 | 1
7 | Generator LLOP Fault | NA | BIT | NA | NA | Input Status | 7 | 1
8 | Alternator Fault | NA | BIT | NA | NA | Input Status | 8 | 1 | Always 0 (Not populated)
9 | Low Fuel Level @ 15% | NA | BIT | NA | NA | Input Status | 9 | 1
10 | Canopy Temp High | NA | BIT | NA | NA | Input Status | 10 | 1
11 | Engine Coolant Temperature High | NA | BIT | NA | NA | Input Status | 11 | 1
12 | Fuel Temperature High | NA | BIT | NA | NA | Input Status | 12 | 1 | Always 0 (Not populated)
13 | Exhaust Temperature High | NA | BIT | NA | NA | Input Status | 13 | 1 | Always 0 (Not populated)
14 | Catalyst Converter Temperature High | NA | BIT | NA | NA | Input Status | 14 | 1 | Always 0 (Not populated)
15 | DG IDLE RUN | NA | BIT | NA | NA | Input Status | 15 | 1
16 | DG Overload | NA | BIT | NA | NA | Input Status | 16 | 1
17 | DG Battery Low | NA | BIT | NA | NA | Input Status | 17 | 1
18 | Water in fuel alarm | NA | BIT | NA | NA | Input Status | 18 | 1 | Always 0 (Not populated)
19 | Water seepage alarm | NA | BIT | NA | NA | Input Status | 19 | 1 | Always 0 (Not populated)
20 | HT Ignition Coil open alarm | NA | BIT | NA | NA | Input Status | 20 | 1 | Always 0 (Not populated)
21 | Spark plug Faulty alarm | NA | BIT | NA | NA | Input Status | 21 | 1 | Always 0 (Not populated)
22 | Air filter choke alarm | NA | BIT | NA | NA | Input Status | 22 | 1 | Always 0 (Not populated)
23 | Gas Filter Choke Alarm | NA | BIT | NA | NA | Input Status | 23 | 1 | Always 0 (Not populated)
24 | Engine Coolant Level Low | NA | BIT | NA | NA | Input Status | 24 | 1 | Always 0 (Not populated)
25 | Gas Leakage Alarm | NA | BIT | NA | NA | Input Status | 25 | 1 | Always 0 (Not populated)
26 | System Shutdown due to Gas leakage | NA | BIT | NA | NA | Input Status | 26 | 1 | Always 0 (Not populated)
27 | Inginition Coil Lead disconnection alarm | NA | BIT | NA | NA | Input Status | 27 | 1 | Always 0 (Not populated)
28 | Generator Maintenance Alarm 50Hrs | NA | BIT | NA | NA | Input Status | 28 | 1
29 | Generator Maintenance Alarm 100Hrs | NA | BIT | NA | NA | Input Status | 29 | 1
30 | Generator Maintenance Alarm 500Hrs | NA | BIT | NA | NA | Input Status | 30 | 1
31 | Generator Maintenance Alarm 1000Hrs | NA | BIT | NA | NA | Input Status | 31 | 1
32 | Generator Maintenance Alarm 2000Hrs | NA | BIT | NA | NA | Input Status | 32 | 1
33 | Low gas pressure at Pilot Regulator output alarm | NA | BIT | NA | NA | Input Status | 33 | 1 | Always 0 (Not populated)
34 | High gas pressure at Pilot Regulator output alarm | NA | BIT | NA | NA | Input Status | 34 | 1 | Always 0 (Not populated)
35 | Vibration sensor ON | NA | BIT | NA | NA | Input Status | 35 | 1 | Always 0 (Not populated)
36 | Radiator Water Level Low | NA | BIT | NA | NA | Input Status | 36 | 1 | Always 0 (Not populated)
37 | Engine Controller Fail alarm | NA | BIT | NA | NA | Input Status | 37 | 1 | Always 0 (Not populated)
38 | Main Controller Fail alarm | NA | BIT | NA | NA | Input Status | 38 | 1
39 | AVR fail alarm | NA | BIT | NA | NA | Input Status | 39 | 1 | Always 0 (Not populated)
40 | PFC Board Fail alarm | NA | BIT | NA | NA | Input Status | 40 | 1 | Always 0 (Not populated)
41 | AVR Excitation Voltage High | NA | BIT | NA | NA | Input Status | 41 | 1 | Always 0 (Not populated)
42 | Over Speed alarm | NA | BIT | NA | NA | Input Status | 42 | 1
43 | Fuel Meter sensing high Consumption than CPH | NA | BIT | NA | NA | Input Status | 43 | 1 | Always 0 (Not populated)
44 | Fuel meter Tamper | NA | BIT | NA | NA | Input Status | 44 | 1 | Always 0 (Not populated)
45 | LLOP Tamper | NA | BIT | NA | NA | Input Status | 45 | 1 | Always 0 (Not populated)
46 | DG Run but no vibration alarm | NA | BIT | NA | NA | Input Status | 46 | 1 | Always 0 (Not populated)
47 | Service Due Alarm | NA | BIT | NA | NA | Input Status | 47 | 1
48 | EGR Warning | NA | BIT | NA | NA | Input Status | 48 | 1
49 | EGR Fault | NA | BIT | NA | NA | Input Status | 49 | 1
50 | NCD Warning | NA | BIT | NA | NA | Input Status | 50 | 1
51 | NCD Fault | NA | BIT | NA | NA | Input Status | 51 | 1
52 | EGR ECU Unhealthy | NA | BIT | NA | NA | Input Status | 52 | 1
52 | EGR Temperature Sensor Open Warning | NA | BIT | NA | NA | Input Status | 53 | 1
53 | EGR Temperature Sensor Faulty Warning | NA | BIT | NA | NA | Input Status | 54 | 1
54 | EGR Valve Open Warning | NA | BIT | NA | NA | Input Status | 55 | 1
55 | EGR Valve Sensor Faulty Warning | NA | BIT | NA | NA | Input Status | 56 | 1
56 | EGR Valve Not Lifting Warning | NA | BIT | NA | NA | Input Status | 57 | 1
57 | EGR Valve Not Closing Warning | NA | BIT | NA | NA | Input Status | 58 | 1
COIL STATUS
1 | DG STOP Command / DG OFF | NA | BIT | NA | NA | Coil Status | 1 | 1
2 | DG START Command / DG ON | NA | BIT | NA | NA | Coil Status | 2 | 1
3 | Auto Mode | NA | BIT | NA | NA | Coil Status | 3 | 1
4 | Manual Mode | NA | BIT | NA | NA | Coil Status | 4 | 1
5 | Future Use | NA | BIT | NA | NA | Coil Status | 5 | 1
6 | Future Use | NA | BIT | NA | NA | Coil Status | 6 | 1
7 | Future Use | NA | BIT | NA | NA | Coil Status | 7 | 1
8 | Future Use | NA | BIT | NA | NA | Coil Status | 8 | 1
9 | Future Use | NA | BIT | NA | NA | Coil Status | 9 | 1
HOLDING REGISTER
1 | DG OP Voltage Low cutoff | Volt | Unsigned Integer | 2 | 1 | Holding Register | 1 | 1
2 | DG OP Voltage High cutoff | Volt | Unsigned Integer | 2 | 1 | Holding Register | 2 | 1
3 | DG start first crank set | Volt | Unsigned Integer | 2 | 1 | Holding Register | 3 | 1
4 | DG start second crank set | Volt | Unsigned Integer | 2 | 1 | Holding Register | 4 | 1 | Always 0xffff (Unused)
5 | DG start third crank set | Volt | Unsigned Integer | 2 | 1 | Holding Register | 5 | 1 | Always 0xffff (Unused)
6 | Rest after first Crank | Volt | Unsigned Integer | 2 | 1 | Holding Register | 6 | 1
7 | Rest after second Crank | Seconds | Unsigned Integer | 2 | 1 | Holding Register | 7 | 1 | Always 0xffff (Unused)
8 | DG Overload Trip | Seconds | Unsigned Integer | 2 | 1 | Holding Register | 8 | 1

## Modbus (For Customer)
Controller: | ECON-MAN-IND
Firmware | v2.04
Protocol | Modbus RTU (RS485)
Sn. | Parameters | Units of | Data Type | Size in byte | Conversion | Type of Register | Modbus | Modbus Register | No. of | Remarks
|  | Measurement | (Float/Hex etc.) |  | Multiplier to read the data |  | Register Address | Actual Implemented in Procom Controller | Registers required |  | Added/Not added
INPUT REGISTER (FC 04)
1 | Product Type (CPCB4 Generator - 20) | NA | Unsigned Integer | 2 | 1 | Input Register | 1 | 0 | 1 | 20->CPCB4 | Added
2 | Product Make | NA | Unsigned Integer | 2 | 1 | Input Register | 2 | 1 | 1 | 100->TMTL 110->M&M 0->Procom | Added (M&M)
3 | Generator Phase (1 for Single Phase 3 for Three Phase) | NA | Unsigned Integer | 2 | 1 | Input Register | 3 | 2 | 1 |  | Added
4 | Fuel Type (Diesel -1 , Gas-2) | NA | Unsigned Integer | 2 | 1 | Input Register | 4 | 3 | 1 | 1->Diesel | Added
5 | Product Rating (Please mention the exact rating) | NA | Unsigned Long Integer | 4 | 0.1 | Input Register | 5 & 6 | 4 & 5 | 2 | Rating in KVA | Added 0xFFFFFFFF
6 | SOFTWARE/FIRMWAREVERSION (Partner Specific) | Version | Unsigned Integer | 2 | 0.01 | Input Register | 7 | 6 | 1 |  | Added fw revision
7 | PROTOCOLVERSION (Indus Priority) - 23 | Version | Unsigned Integer | 2 | 1 | Input Register | 8 | 7 | 1 |  | Added 1
8 | Genset Serial No | NA | ASCII String | 20 | NA | Input Register | 2018-09-01 | 8-17 | 10 | Max 19 characters (null-terminated) (Reserved for now) | Reserved
9 | Engine Serial No | NA | ASCII String | 20 | NA | Input Register | 19-28 | 18-27 | 10 | Max 19 characters (null-terminated) (Reserved for now) | Reserved
10 | Alternator Serial No | NA | ASCII String | 20 | NA | Input Register | 29-38 | 28-37 | 10 | Max 19 characters (null-terminated) (Reserved for now) | Reserved
11 | Main Controller Serial No | NA | ASCII String | 20 | NA | Input Register | 40-49 | 39-48 | 10 | Max 19 characters (null-terminated) (Reserved for now) | Reserved
12 | Engine Controller Serial No | NA | ASCII String | 20 | NA | Input Register | 50-59 | 49-58 | 10 | Max 19 characters (null-terminated) (Reserved for now) | Reserved
13 | SITE ID | NA | ASCII String | 10 | NA | Input Register | 60-64 | 59-63 | 5 | Max 19 characters (null-terminated). But only the first 9 characters are shown if it's length exceeds 9 character. (Reserved for now) | Reserved
14 | DATE | Date | Unsigned Integer | 2 | 1 | Input Register | 65 | 64 | 1 | Current Date | Added
15 | HOUR | Hour | Unsigned Integer | 2 | 1 | Input Register | 66 | 65 | 1 | Current Hour | Added
16 | MINUTES | Minutes | Unsigned Integer | 2 | 1 | Input Register | 67 | 66 | 1 | Current Minutes | Added
17 | SECONDS | Seconds | Unsigned Integer | 2 | 1 | Input Register | 68 | 67 | 1 | Current Seconds | Added
18 | MONTH | Month | Unsigned Integer | 2 | 1 | Input Register | 69 | 68 | 1 | Current Month | Added
19 | YEAR | Year | Unsigned Integer | 2 | 1 | Input Register | 70 | 69 | 1 | Current Year | Added
20 | Generator R Phase Voltage | Volt | Unsigned Integer | 2 | 0.01 | Input Register | 71 | 70 | 1 |  | Added
21 | Generator Y Phase Voltage | Volt | Unsigned Integer | 2 | 0.01 | Input Register | 72 | 71 | 1 |  | Added
22 | Generator B Phase Voltage | Volt | Unsigned Integer | 2 | 0.01 | Input Register | 73 | 72 | 1 |  | Added
23 | Generator Line Voltage RY | Volt | Unsigned Integer | 2 | 0.01 | Input Register | 74 | 73 | 1 |  | Added
24 | Generator Line Voltage YB | Volt | Unsigned Integer | 2 | 0.01 | Input Register | 75 | 74 | 1 |  | Added
25 | Generator Line Voltage BR | Volt | Unsigned Integer | 2 | 0.01 | Input Register | 76 | 75 | 1 |  | Added
26 | Generator Frequency | Hz | Unsigned Integer | 2 | 0.01 | Input Register | 77 | 76 | 1 |  | Added
27 | N-E (Neutral to Earth) Voltage | Volt | Unsigned Integer | 2 | 0.01 | Input Register | 78 | 77 | 1 | Always 0 (Not populated) | Added
28 | Load Current R Phase | Amps | Unsigned Integer | 2 | 0.01 | Input Register | 79 | 78 | 1 |  | Added
29 | Load Current Y Phase | Amps | Unsigned Integer | 2 | 0.01 | Input Register | 80 | 79 | 1 |  | Added
30 | Load Current B Phase | Amps | Unsigned Integer | 2 | 0.01 | Input Register | 81 | 80 | 1 |  | Added
31 | Total Load Current | Amps | Unsigned Integer | 2 | 0.01 | Input Register | 82 | 81 | 1 |  | Added, sum of 3 load currents
32 | R Phase Power Factor | PF | Unsigned Integer | 2 | 0.01 | Input Register | 83 | 82 | 1 |  | Added
33 | Y Phase Power Factor | PF | Unsigned Integer | 2 | 0.01 | Input Register | 84 | 83 | 1 |  | Added
34 | B Phase Power Factor | PF | Unsigned Integer | 2 | 0.01 | Input Register | 85 | 84 | 1 |  | Added
35 | Engine Speed (RPM) | RPM | Unsigned Long Integer | 4 | 1 | Input Register | 86- 87 | 85-86 | 2 |  | Added
36 | Generator Total Run Hours | Hour | Unsigned Long Integer | 4 | 0.1 | Input Register | 88- 89 | 87-88 | 2 | Doesn't include Tamper run hours | Added
37 | Generator Remote Run Hours | Hour | Unsigned Long Integer | 4 | 0.1 | Input Register | 90- 91 | 89-90 | 2 | Doesn't include Tamper run hours | Not added
38 | Generator Manual Run Hours | Hour | Unsigned Long Integer | 4 | 0.1 | Input Register | 92- 93 | 91-92 | 2 | Doesn't include Tamper run hours | Not added
39 | Generator No Load Run Hours | Hour | Unsigned Long Integer | 4 | 0.1 | Input Register | 94- 95 | 93-94 | 2 | Doesn't include Tamper run hours | Not added
40 | Generator ON Load Run Hours | Hour | Unsigned Long Integer | 4 | 0.1 | Input Register | 96-97 | 95-96 | 2 | Doesn't include Tamper run hours | Not added
41 | Generator Output Power - Real | KW | Unsigned Integer | 2 | 0.01 | Input Register | 98 | 97 | 1 |  | Added
42 | Generator Output Power - Apparent | KVA | Unsigned Integer | 2 | 0.01 | Input Register | 99 | 98 | 1 |  | Added
43 | Generator Output Power - Reactive | KVAR | Unsigned Integer | 2 | 0.01 | Input Register | 100 | 99 | 1 |  | Added
44 | Total Generator Energy | KWH | Unsigned Long Integer | 4 | 0.01 | Input Register | 101-102 | 100-101 | 2 | Doesn't include Tamper KWh | Added
45 | Canopy Temperature (above Engine) | Degree C | Unsigned Integer | 2 | 0.1 | Input Register | 103 | 102 | 1 | Always 0xffff (Not populated) | Added
46 | Canopy Temperature (far end side from Radiator) | Degree C | Unsigned Integer | 2 | 0.1 | Input Register | 104 | 103 | 1 |  | Added
47 | Air Inlet Temperature | Degree C | Unsigned Integer | 2 | 0.1 | Input Register | 105 | 104 | 1 | Always 0xffff (Not populated) | Added
48 | Fuel Temperature | Degree C | Unsigned Integer | 2 | 0.1 | Input Register | 106 | 105 | 1 | Always 0xffff (Not populated) | Added
49 | Exhaust Temperature | Degree C | Unsigned Long Integer | 4 | 0.1 | Input Register | 107-108 | 106-107 | 2 | Always 0xffffffff (Not populated) | Added
50 | Catalyst Converter Temperature | Degree C | Unsigned | 4 | 0.1 | Input Register | 109-110 | 108-109 | 2 | Always 0xffffffff (Not populated) | Added
51 | Engine Coolant Temp | Degree C | Unsigned Long Integer | 4 | 0.1 | Input Register | 111-112 | 110-111 | 2 | 0xffffffff when Sensor Open or if sensor is disabled | Added
52 | Radiator Coolant Temp - inlet | Degree C | Unsigned Long Integer | 4 | 0.1 | Input Register | 113-114 | 112-113 | 2 | Always 0xffffffff (Not populated) | Added
53 | Radiator Coolant Temp - outlet | Degree C | Unsigned Long Integer | 4 | 0.1 | Input Register | 115-116 | 114-116 | 2 | Always 0xffffffff (Not populated) | Added
54 | Stop Solenoid Body Temperature | Degree C | Unsigned Long Integer | 4 | 0.1 | Input Register | 117-118 | 116-117 | 2 | Always 0xffffffff (Not populated) | Added
55 | LLOP (Low Lube oil pressure) | psi | Unsigned Integer | 2 | 0.01 | Input Register | 119 | 118 | 1 | 0xffff when Sensor Open or if sensor is disabled This is LOP | Added
56 | Generator Battery Voltage | Volt | Unsigned Integer | 2 | 0.01 | Input Register | 120 | 119 | 1 |  | Added
57 | Fuel Level % | % | Unsigned Integer | 2 | 0.01 | Input Register | 121 | 120 | 1 | 0xffffffff when Sensor Open or if sensor id disabled | Added
58 | Fuel Consumed in liter | Liter | Unsigned Long Integer | 4 | 0.01 | Input Register | 122-123 | 121-121 | 2 | Always 0xffffffff (Not populated) | Added
59 | Gas Consumed in SCM | SCM | Unsigned Long Integer | 4 | 0.01 | Input Register | 124-125 | 123-124 | 2 | Always 0xffffffff (Not populated) | Added
60 | Total no of Cranks | Nos | Unsigned Long Integer | 4 | 0.01 | Input Register | 126-127 | 125-126 | 2 |  | Not added
61 | No of Cranks failed attempt | Nos | Unsigned Long Integer | 4 | 0.01 | Input Register | 128-129 | 127-128 | 2 |  | Not added
62 | Air Inlet Pressure | mBar | Unsigned Integer | 2 | 0.01 | Input Register | 130 | 129 | 1 | Always 0xffff (Not populated) | Added
63 | Engine Oil Level % | % | Unsigned Integer | 2 | 0.01 | Input Register | 131 | 130 | 1 | Always 0xffff (Not populated) | Added
64 | Turbo Oil Pressure | mBar | Unsigned Integer | 2 | 0.01 | Input Register | 132 | 131 | 1 | Always 0xffff (Not populated) | Added
65 | Engine Coolant Level % | % | Unsigned Integer | 2 | 0.01 | Input Register | 133 | 132 | 1 | Always 0xffff (Not populated) | Added
66 | Pilot Regulator input Pressure | mBar | Unsigned Integer | 2 | 0.01 | Input Register | 134 | 133 | 1 | Always 0xffff (Not populated) | Added
67 | Pilot Regulator output Pressure | mBar | Unsigned Integer | 2 | 0.01 | Input Register | 135 | 134 | 1 | Always 0xffff (Not populated) | Added
68 | Engine (Gas or Diesel) (For Diesel- 1 and Gas- 2) | NA | Unsigned Integer | 2 | 1 | Input Register | 136 | 135 | 1 | 1->Diesel | Added
69 | DG Vibration Sensor output in kHz or Volt |  | Unsigned Integer | 2 | 0.01 | Input Register | 137 | 136 | 1 | Always 0xffff (Not populated) | Added
70 | Radiator Water Level | % | Unsigned Integer | 2 | 0.01 | Input Register | 138 | 137 | 1 | Always 0xffff (Not populated) | Added
71 | NTP Factor Auto Calculation | Nos | Unsigned Integer | 2 | 0.01 | Input Register | 139 | 138 | 1 | Always 0xffff (Not populated) | Added
72 | AVR Excitation Voltage | Volt | Unsigned Integer | 2 | 0.01 | Input Register | 140 | 139 | 1 | Always 0xffff (Not populated) | Added
73 | Lube Oil Viscosity | mm2/S | Unsigned Integer | 2 | 0.01 | Input Register | 141 | 140 | 1 | Always 0xffff (Not populated) | Added
74 | Started on Remote mode or Manual | NA | Unsigned Integer | 2 | 1 | Input Register | 142 | 141 | 1 | 0->Manual Mode 1->Remote Mode | Added
| Mode (Remoe Mode-1,Manual Mode- 0) | [9 empty] | Added
75 | DG On Trigger due to Battery Volt. or Shelter Temp. (Battery - 1, temp-2) | NA | Unsigned Integer | 2 | 1 | Input Register | 143 | 142 | 1 | Always 0xffff (Not populated) | Added
76 | Reserved |  |  | 4 |  | Input Register | 144 | 143 | 2 |  | Added
77 | Reserved |  |  | 4 |  | Input Register | 146 | 145 | 2 |  | Added
78 | Reserved |  |  | 4 |  | Input Register | 148 | 147 | 2 |  | Added
79 | Reserved |  |  | 4 |  | Input Register | 150 | 149 | 2 |  | Added
80 | Reserved |  |  | 4 |  | Input Register | 152 | 151 | 2 |  | Added
81 | Reserved |  |  | 2 |  | Input Register | 154 | 153 | 1 |  | Added
82 | Reserved |  |  | 2 |  | Input Register | 155 | 154 | 1 |  | Added
83 | Reserved |  |  | 2 |  | Input Register | 156 | 155 | 1 |  | Added
84 | Reserved |  |  | 4 |  | Input Register | 157-158 | 156-157 | 2 |  | Added
85 | Reserved |  |  | 4 |  | Input Register | 159-160 | 158-159 | 2 |  | Added
86 | Reserved |  |  | 4 |  | Input Register | 161-162 | 160-161 | 2 |  | Added
87 | NCD Error Hrs | Hour | Unsigned Long Integer | 4 | 0.1 | Input Register | 163-164 | 162-163 | 2 |  | Added
88 | NCD Heal Hrs | Hour | Unsigned Long Integer | 4 | 0.1 | Input Register | 165-166 | 164-165 | 2 |  | Added
INPUT STATUS (FC 02)
1 | Fire/Smoke | NA | BIT | NA | NA | Input Status | 1 | 0 | 1 |  | Added
2 | Canopy Door Open | NA | BIT | NA | NA | Input Status | 2 | 1 | 1 |  | Added
3 | Load on Generator | NA | BIT | NA | NA | Input Status | 3 | 2 | 1 |  | Added
4 | Generator Fail to Start | NA | BIT | NA | NA | Input Status | 4 | 3 | 1 |  | Added
5 | Generator Fail to Stop | NA | BIT | NA | NA | Input Status | 5 | 4 | 1 |  | Added
6 | Generator Common Fault | NA | BIT | NA | NA | Input Status | 6 | 5 | 1 |  | Added
7 | Generator LLOP Fault | NA | BIT | NA | NA | Input Status | 7 | 6 | 1 |  | Added
8 | Alternator Fault | NA | BIT | NA | NA | Input Status | 8 | 7 | 1 | Always 0 (Not populated) | Added
9 | Low Fuel Level @ 15% | NA | BIT | NA | NA | Input Status | 9 | 8 | 1 |  | Added
10 | Canopy Temp High | NA | BIT | NA | NA | Input Status | 10 | 9 | 1 |  | Added
11 | Engine Coolant Temperature High | NA | BIT | NA | NA | Input Status | 11 | 10 | 1 |  | Added
12 | Fuel Temperature High | NA | BIT | NA | NA | Input Status | 12 | 11 | 1 | Always 0 (Not populated) | Added
13 | Exhaust Temperature High | NA | BIT | NA | NA | Input Status | 13 | 12 | 1 | Always 0 (Not populated) | Added
14 | Catalyst Converter Temperature High | NA | BIT | NA | NA | Input Status | 14 | 13 | 1 | Always 0 (Not populated) | Added
15 | DG IDLE RUN | NA | BIT | NA | NA | Input Status | 15 | 14 | 1 |  | Added
16 | DG Overload | NA | BIT | NA | NA | Input Status | 16 | 15 | 1 |  | Added
17 | DG Battery Low | NA | BIT | NA | NA | Input Status | 17 | 16 | 1 |  | Added
18 | Water in fuel alarm | NA | BIT | NA | NA | Input Status | 18 | 17 | 1 | Always 0 (Not populated) | Added
19 | Water seepage alarm | NA | BIT | NA | NA | Input Status | 19 | 18 | 1 | Always 0 (Not populated) | Added
20 | HT Ignition Coil open alarm | NA | BIT | NA | NA | Input Status | 20 | 19 | 1 | Always 0 (Not populated) | Added
21 | Spark plug Faulty alarm | NA | BIT | NA | NA | Input Status | 21 | 20 | 1 | Always 0 (Not populated) | Added
22 | Air filter choke alarm | NA | BIT | NA | NA | Input Status | 22 | 21 | 1 | Always 0 (Not populated) | Added
23 | Gas Filter Choke Alarm | NA | BIT | NA | NA | Input Status | 23 | 22 | 1 | Always 0 (Not populated) | Added
24 | Engine Coolant Level Low | NA | BIT | NA | NA | Input Status | 24 | 23 | 1 | Always 0 (Not populated) | Added
25 | Gas Leakage Alarm | NA | BIT | NA | NA | Input Status | 25 | 24 | 1 | Always 0 (Not populated) | Added
26 | System Shutdown due to Gas leakage | NA | BIT | NA | NA | Input Status | 26 | 25 | 1 | Always 0 (Not populated) | Added
27 | Inginition Coil Lead disconnection alarm | NA | BIT | NA | NA | Input Status | 27 | 26 | 1 | Always 0 (Not populated) | Added
28 | Generator Maintenance Alarm 50Hrs | NA | BIT | NA | NA | Input Status | 28 | 27 | 1 |  | Added
29 | Generator Maintenance Alarm 100Hrs | NA | BIT | NA | NA | Input Status | 29 | 28 | 1 |  | Added
30 | Generator Maintenance Alarm 500Hrs | NA | BIT | NA | NA | Input Status | 30 | 29 | 1 |  | Added
31 | Generator Maintenance Alarm 1000Hrs | NA | BIT | NA | NA | Input Status | 31 | 30 | 1 |  | Added
32 | Generator Maintenance Alarm 2000Hrs | NA | BIT | NA | NA | Input Status | 32 | 31 | 1 |  | Added
33 | Low gas pressure at Pilot Regulator output alarm | NA | BIT | NA | NA | Input Status | 33 | 32 | 1 | Always 0 (Not populated) | Added
34 | High gas pressure at Pilot Regulator output alarm | NA | BIT | NA | NA | Input Status | 34 | 33 | 1 | Always 0 (Not populated) | Added
35 | Vibration sensor ON | NA | BIT | NA | NA | Input Status | 35 | 34 | 1 | Always 0 (Not populated) | Added
36 | Radiator Water Level Low | NA | BIT | NA | NA | Input Status | 36 | 35 | 1 | Always 0 (Not populated) | Added
37 | Engine Controller Fail alarm | NA | BIT | NA | NA | Input Status | 37 | 36 | 1 | Always 0 (Not populated) | Added
38 | Main Controller Fail alarm | NA | BIT | NA | NA | Input Status | 38 | 37 | 1 |  | Added
39 | AVR fail alarm | NA | BIT | NA | NA | Input Status | 39 | 38 | 1 | Always 0 (Not populated) | Added
40 | PFC Board Fail alarm | NA | BIT | NA | NA | Input Status | 40 | 39 | 1 | Always 0 (Not populated) | Added
41 | AVR Excitation Voltage High | NA | BIT | NA | NA | Input Status | 41 | 40 | 1 | Always 0 (Not populated) | Added
42 | Over Speed alarm | NA | BIT | NA | NA | Input Status | 42 | 41 | 1 |  | Added
43 | Fuel Meter sensing high Consumption than CPH | NA | BIT | NA | NA | Input Status | 43 | 42 | 1 | Always 0 (Not populated) | Added
44 | Fuel meter Tamper | NA | BIT | NA | NA | Input Status | 44 | 43 | 1 | Always 0 (Not populated) | Added
45 | LLOP Tamper | NA | BIT | NA | NA | Input Status | 45 | 44 | 1 | Always 0 (Not populated) | Added
46 | DG Run but no vibration alarm | NA | BIT | NA | NA | Input Status | 46 | 45 | 1 | Always 0 (Not populated) | Added
47 | Reserved | NA | BIT | NA | NA | Input Status | 47 | 46 | 1 |  | Added
48 | EGR Warning | NA | BIT | NA | NA | Input Status | 48 | 47 | 1 |  | Added
49 | EGR Fault | NA | BIT | NA | NA | Input Status | 49 | 48 | 1 |  | Added
50 | NCD Warning | NA | BIT | NA | NA | Input Status | 50 | 49 | 1 |  | TBD
51 | NCD Fault | NA | BIT | NA | NA | Input Status | 51 | 50 | 1 |  | TBD
52 | EGR ECU Unhealthy | NA | BIT | NA | NA | Input Status | 52 | 51 | 1 |  | Added
53 | EGR Temperature Sensor Open Warning | NA | BIT | NA | NA | Input Status | 53 | 52 | 1 |  | Added
54 | EGR Temperature Sensor Faulty Warning | NA | BIT | NA | NA | Input Status | 54 | 53 | 1 |  | Added
55 | EGR Valve Open Warning | NA | BIT | NA | NA | Input Status | 55 | 54 | 1 |  | Added
56 | EGR Valve Sensor Faulty Warning | NA | BIT | NA | NA | Input Status | 56 | 55 | 1 |  | Added
57 | EGR Valve Not Lifting Warning | NA | BIT | NA | NA | Input Status | 57 | 56 | 1 |  | Added
58 | EGR Valve Not Closing Warning | NA | BIT | NA | NA | Input Status | 58 | 57 | 1 |  | Added
COIL STATUS (FC 01)
1 | DG STOP Command / DG OFF | NA | BIT | NA | NA | Coil Status | 1 | 0 | 1 |  | Added
2 | DG START Command / DG ON | NA | BIT | NA | NA | Coil Status | 2 | 1 | 1 |  | Added
3 | Remote Mode | NA | BIT | NA | NA | Coil Status | 3 | 2 | 1 |  | Added
4 | Manual Mode | NA | BIT | NA | NA | Coil Status | 4 | 3 | 1 |  | Added
5 | Future Use | NA | BIT | NA | NA | Coil Status | 5 | 4 | 1 |  | Added
6 | Future Use | NA | BIT | NA | NA | Coil Status | 6 | 5 | 1 |  | Added
7 | Future Use | NA | BIT | NA | NA | Coil Status | 7 | 6 | 1 |  | Added
8 | Future Use | NA | BIT | NA | NA | Coil Status | 8 | 7 | 1 |  | Added
9 | Future Use | NA | BIT | NA | NA | Coil Status | 9 | 8 | 1 |  | Added
HOLDING REGISTER (FC 03)
1 | DG OP Voltage Low cutoff | Volt | Unsigned Integer | 2 | 1 | Holding Register | 1 | 0 | 1 |  | Added
2 | DG OP Voltage High cutoff | Volt | Unsigned Integer | 2 | 1 | Holding Register | 2 | 1 | 1 |  | Added
3 | DG start first crank set | Seconds | Unsigned Integer | 2 | 1 | Holding Register | 3 | 2 | 1 |  | Added
4 | DG start second crank set | Seconds | Unsigned Integer | 2 | 1 | Holding Register | 4 | 3 | 1 | Always 0xffff (Unused) | Added
5 | DG start third crank set | Seconds | Unsigned Integer | 2 | 1 | Holding Register | 5 | 4 | 1 | Always 0xffff (Unused) | Added
6 | Rest after first Crank | Seconds | Unsigned Integer | 2 | 1 | Holding Register | 6 | 5 | 1 |  | Added
7 | Rest after second Crank | Seconds | Unsigned Integer | 2 | 1 | Holding Register | 7 | 6 | 1 | Always 0xffff (Unused) | Added
8 | DG Overload Trip | Seconds | Unsigned Integer | 2 | 1 | Holding Register | 8 | 7 | 1 |  | Added

## Modbus Example (TMTL) (hidden)
Controller: | ECON-MAN-IND
Firmware | v2.04
Protocol | Modbus RTU (RS485)
Sn. | Parameters | Units of | Data Type | Size in byte | Conversion | Type of Register | Modbus | No. of | Remarks | Raw Data in Example | Calculated Data in Example
|  | Measurement | (Float/Hex etc.) |  | Multiplier to read the data |  | Register Address | Registers required
INPUT REGISTER
1 | Product Type (CPCB4 - 20) | NA | Unsigned Integer | 2 | 1 | Input Register | 1 | 1 | 20->CPCB4 | 20 | CPCB4 Generator
2 | Product Make | NA | Unsigned Integer | 2 | 1 | Input Register | 2 | 1 | 100->TMTL 110->M&M 0->Procom | 100 | TMTL
3 | Generator Phase (1 for Single Phase 3 for Three Phase) | NA | Unsigned Integer | 2 | 1 | Input Register | 3 | 1 |  | 1 | Single Phase Generator
4 | Fuel Type (Diesel -1 , Gas-2) | NA | Unsigned Integer | 2 | 1 | Input Register | 4 | 1 | 1->Diesel | 1 | Diesel
5 | Product Rating (Please mention the exact rating) | NA | Unsigned Long Integer | 4 | 0.1 | Input Register | 5 & 6 | 2 | Rating in KVA | 150 | 15.0KVA
6 | SOFTWARE/FIRMWAREVERSION (Partner Specific) | Version | Unsigned Integer | 2 | 0.01 | Input Register | 7 | 1 |  | 200 | 2
7 | PROTOCOLVERSION (Indus Priority) - 23 | Version | Unsigned Integer | 2 | 1 | Input Register | 8 | 1 |  | 23 | 23
8 | Genset Serial No | NA | ASCII String | 20 | NA | Input Register | 9-18 | 10 | Max 19 characters (null-terminated) | 0x32323041302D454730313500000000000000 | "220A0-EG015"
9 | Engine Serial No | NA | ASCII String | 20 | NA | Input Register | 19-28 | 10 | Max 19 characters (null-terminated) | 0x353333343234303533303132000000000000 | "533424053012"
10 | Alternator Serial No | NA | ASCII String | 20 | NA | Input Register | 29-38 | 10 | Max 19 characters (null-terminated) | 0x333233493339333139340000000000000000 | "323I393194"
11 | Main Controller Serial No | NA | ASCII String | 20 | NA | Input Register | 40-49 | 10 | Max 19 characters (null-terminated) | 0x000000000000000000000000000000000000 | ""
12 | Engine Controller Serial No | NA | ASCII String | 20 | NA | Input Register | 50-59 | 10 | Max 19 characters (null-terminated) | 0x000000000000000000000000000000000000 | ""
13 | SITE ID | NA | ASCII String | 10 | NA | Input Register | 60-64 | 5 | Max 19 characters (null-terminated). But only the first 9 characters are shown if it's length exceeds 9 character. | 0x4A43 | JC
14 | DATE | Date | Unsigned Integer | 2 | 1 | Input Register | 65 | 1 | Current Date | 10 | 10
15 | HOUR | Hour | Unsigned Integer | 2 | 1 | Input Register | 66 | 1 | Current Hour | 16 | 16
16 | MINUTES | Minutes | Unsigned Integer | 2 | 1 | Input Register | 67 | 1 | Current Minutes | 49 | 49
17 | SECONDS | Seconds | Unsigned Integer | 2 | 1 | Input Register | 68 | 1 | Current Seconds | 14 | 14
18 | MONTH | Month | Unsigned Integer | 2 | 1 | Input Register | 69 | 1 | Current Month | 1 | January
19 | YEAR | Year | Unsigned Integer | 2 | 1 | Input Register | 70 | 1 | Current Year | 2024 | 2024
20 | Generator R Phase Voltage | Volt | Unsigned Integer | 2 | 0.01 | Input Register | 71 | 1 |  | 23080 | 230.80V
21 | Generator Y Phase Voltage | Volt | Unsigned Integer | 2 | 0.01 | Input Register | 72 | 1 |  | 0 | 0V
22 | Generator B Phase Voltage | Volt | Unsigned Integer | 2 | 0.01 | Input Register | 73 | 1 |  | 0 | 0V
23 | Generator Line Voltage RY | Volt | Unsigned Integer | 2 | 0.01 | Input Register | 74 | 1 |  | 0 | 0V
24 | Generator Line Voltage YB | Volt | Unsigned Integer | 2 | 0.01 | Input Register | 75 | 1 |  | 0 | 0V
25 | Generator Line Voltage BR | Volt | Unsigned Integer | 2 | 0.01 | Input Register | 76 | 1 |  | 0 | 0V
26 | Generator Frequency | Hz | Unsigned Integer | 2 | 0.01 | Input Register | 77 | 1 |  | 5040 | 50.40Hz
27 | N-E (Neutral to Earth) Voltage | Volt | Unsigned Integer | 2 | 0.01 | Input Register | 78 | 1 | Always 0 (Not populated) | 0 | (Not supported)
28 | Load Current R Phase | Amps | Unsigned Integer | 2 | 0.01 | Input Register | 79 | 1 |  | 1368 | 13.68A
29 | Load Current Y Phase | Amps | Unsigned Integer | 2 | 0.01 | Input Register | 80 | 1 |  | 0 | 0A
30 | Load Current B Phase | Amps | Unsigned Integer | 2 | 0.01 | Input Register | 81 | 1 |  | 0 | 0A
31 | Total Load Current | Amps | Unsigned Integer | 2 | 0.01 | Input Register | 82 | 1 |  | 1368 | 13.68A
32 | R Phase Power Factor | PF | Unsigned Integer | 2 | 0.01 | Input Register | 83 | 1 |  | 100 | 1
33 | Y Phase Power Factor | PF | Unsigned Integer | 2 | 0.01 | Input Register | 84 | 1 |  | 100 | 1
34 | B Phase Power Factor | PF | Unsigned Integer | 2 | 0.01 | Input Register | 85 | 1 |  | 100 | 1
35 | Engine Speed (RPM) | RPM | Unsigned Long Integer | 4 | 1 | Input Register | 86- 87 | 2 |  | 1512 | 1512 RPM
36 | Generator Total Run Hours | Hour | Unsigned Long Integer | 4 | 0.1 | Input Register | 88- 89 | 2 | Doesn't include Tamper run hours | 22 | 2.2Hrs
37 | Generator Remote Run Hours | Hour | Unsigned Long Integer | 4 | 0.1 | Input Register | 90- 91 | 2 | Doesn't include Tamper run hours | 0 | 0 Hrs
38 | Generator Manual Run Hours | Hour | Unsigned Long Integer | 4 | 0.1 | Input Register | 92- 93 | 2 | Doesn't include Tamper run hours | 22 | 2.2Hrs
39 | Generator No Load Run Hours | Hour | Unsigned Long Integer | 4 | 0.1 | Input Register | 94- 95 | 2 | Doesn't include Tamper run hours | 6 | 0.6 Hrs
40 | Generator ON Load Run Hours | Hour | Unsigned Long Integer | 4 | 0.1 | Input Register | 96-97 | 2 | Doesn't include Tamper run hours | 16 | 1.6Hrs
41 | Generator Output Power - Real | KW | Unsigned Integer | 2 | 0.01 | Input Register | 98 | 1 |  | 324 | 3.24KW
42 | Generator Output Power - Apparent | KVA | Unsigned Integer | 2 | 0.01 | Input Register | 99 | 1 |  | 324 | 3.24KVA
43 | Generator Output Power - Reactive | KVAR | Unsigned Integer | 2 | 0.01 | Input Register | 100 | 1 |  | 0 | 0
44 | Total Generator Energy | KWH | Unsigned Long Integer | 4 | 0.01 | Input Register | 101-102 | 2 |  | 590 | 5.90KWH
45 | Canopy Temperature (above Engine) | Degree C | Unsigned Integer | 2 | 0.1 | Input Register | 103 | 1 | Always 0xffff (Not populated) | -1 | (Not supported)
46 | Canopy Temperature (far end side from Radiator) | Degree C | Unsigned Integer | 2 | 0.1 | Input Register | 104 | 1 |  | 199 | 19.9 C
47 | Air Inlet Temperature | Degree C | Unsigned Integer | 2 | 0.1 | Input Register | 105 | 1 | Always 0xffff (Not populated) | -1 | (Not supported)
48 | Fuel Temperature | Degree C | Unsigned Integer | 2 | 0.1 | Input Register | 106 | 1 | Always 0xffff (Not populated) | -1 | (Not supported)
49 | Exhaust Temperature | Degree C | Unsigned Long Integer | 4 | 0.1 | Input Register | 107-108 | 2 | Always 0xffffffff (Not populated) | -1 | (Not supported)
50 | Catalyst Converter Temperature | Degree C | Unsigned | 4 | 0.1 | Input Register | 109-110 | 2 | Always 0xffffffff (Not populated) | -1 | (Not supported)
51 | Engine Coolant Temp | Degree C | Unsigned Long Integer | 4 | 0.1 | Input Register | 111-112 | 2 | 0xffffffff when Sensor Open | 960 | 96.0 C
52 | Radiator Coolant Temp - inlet | Degree C | Unsigned Long Integer | 4 | 0.1 | Input Register | 113-114 | 2 | Always 0xffffffff (Not populated) | -1 | (Not supported)
53 | Radiator Coolant Temp - outlet | Degree C | Unsigned Long Integer | 4 | 0.1 | Input Register | 115-116 | 2 | Always 0xffffffff (Not populated) | -1 | (Not supported)
54 | Stop Solenoid Body Temperature | Degree C | Unsigned Long Integer | 4 | 0.1 | Input Register | 117-118 | 2 | Always 0xffffffff (Not populated) | -1 | (Not supported)
55 | LLOP (Low Lube oil pressure) | psi | Unsigned Integer | 2 | 0.01 | Input Register | 119 | 1 | 0xffff when Sensor Open | 4551 | 45.51 psi
56 | Generator Battery Voltage | Volt | Unsigned Integer | 2 | 0.01 | Input Register | 120 | 1 |  | 1550 | 15.50 V
57 | Fuel Level % | % | Unsigned Integer | 2 | 0.01 | Input Register | 121 | 1 | 0xffffffff when Sensor Open | -1 | Sensor Open
58 | Fuel Consumed in liter | Liter | Unsigned Long Integer | 4 | 0.01 | Input Register | 122-123 | 2 | Always 0xffffffff (Not populated) | -1 | (Not supported)
59 | Gas Consumed in SCM | SCM | Unsigned Long Integer | 4 | 0.01 | Input Register | 124-125 | 2 | Always 0xffffffff (Not populated) | -1 | (Not supported)
60 | Total no of Cranks | Nos | Unsigned Long Integer | 4 | 0.01 | Input Register | 126-127 | 2 |  | 0x1BBC | 71
61 | No of Cranks failed attempt | Nos | Unsigned Long Integer | 4 | 0.01 | Input Register | 128-129 | 2 |  | 0x898 | 22
62 | Air Inlet Pressure | mBar | Unsigned Integer | 2 | 0.01 | Input Register | 130 | 1 | Always 0xffff (Not populated) | 0xffff | (Not supported)
63 | Engine Oil Level % | % | Unsigned Integer | 2 | 0.01 | Input Register | 131 | 1 | Always 0xffff (Not populated) | 0xffff | (Not supported)
64 | Turbo Oil Pressure | mBar | Unsigned Integer | 2 | 0.01 | Input Register | 132 | 1 | Always 0xffff (Not populated) | 0xffff | (Not supported)
65 | Engine Coolant Level % | % | Unsigned Integer | 2 | 0.01 | Input Register | 133 | 1 | Always 0xffff (Not populated) | 0xffff | (Not supported)
66 | Pilot Regulator input Pressure | mBar | Unsigned Integer | 2 | 0.01 | Input Register | 134 | 1 | Always 0xffff (Not populated) | 0xffff | (Not supported)
67 | Pilot Regulator output Pressure | mBar | Unsigned Integer | 2 | 0.01 | Input Register | 135 | 1 | Always 0xffff (Not populated) | 0xffff | (Not supported)
68 | Engine (Gas or Diesel) (For Diesel- 1 and Gas- 2) | NA | Unsigned Integer | 2 | 1 | Input Register | 136 | 1 | 1->Diesel | 1 | Diesel
69 | DG Vibration Sensor output in kHz or Volt |  | Unsigned Integer | 2 | 0.01 | Input Register | 137 | 1 | Always 0xffff (Not populated) | 0xffff | (Not supported)
70 | Radiator Water Level | % | Unsigned Integer | 2 | 0.01 | Input Register | 138 | 1 | Always 0xffff (Not populated) | 0xffff | (Not supported)
71 | NTP Factor Auto Calculation | Nos | Unsigned Integer | 2 | 0.01 | Input Register | 139 | 1 | Always 0xffff (Not populated) | 0xffff | (Not supported)
72 | AVR Excitation Voltage | Volt | Unsigned Integer | 2 | 0.01 | Input Register | 140 | 1 | Always 0xffff (Not populated) | 0xffff | (Not supported)
73 | Lube Oil Viscosity | mm2/S | Unsigned Integer | 2 | 0.01 | Input Register | 141 | 1 | Always 0xffff (Not populated) | 0xffff | (Not supported)
74 | Started on Auto mode or Manual | NA | Unsigned Integer | 2 | 1 | Input Register | 142 | 1 | 0->Manual Mode 1->Remote Mode | 0 | Started on Manual Mode
Mode (Remote mode-1,Manual Mode- 0)
75 | DG On Trigger due to Battery Volt. or Shelter Temp. (Battery - 1, temp-2) | NA | Unsigned Integer | 2 | 1 | Input Register | 143 | 1 | Always 0xffff (Not populated) | 0xffff | (Not supported)
76 | Reserved |  |  | 4 |  | Input Register | 144 | 2 | Reserved | Reserved | Reserved
77 | Reserved |  |  | 4 |  | Input Register | 146 | 2 | Reserved | Reserved | Reserved
78 | Reserved |  |  | 4 |  | Input Register | 148 | 2 | Reserved | Reserved | Reserved
79 | Reserved |  |  | 4 |  | Input Register | 150 | 2 | Reserved | Reserved | Reserved
80 | Reserved |  |  | 4 |  | Input Register | 152 | 2 | Reserved | Reserved | Reserved
81 | Reserved |  |  | 2 |  | Input Register | 154 | 1 | Reserved | Reserved | Reserved
82 | Reserved |  |  | 2 |  | Input Register | 155 | 1 | Reserved | Reserved | Reserved
83 | Reserved |  |  | 2 |  | Input Register | 156 | 1 | Reserved | Reserved | Reserved
84 | Reserved |  |  | 4 |  | Input Register | 157-158 | 2 | Reserved | Reserved | Reserved
85 | Reserved |  |  | 4 |  | Input Register | 159-160 | 2 | Reserved | Reserved | Reserved
86 | Reserved |  |  | 4 |  | Input Register | 161-162 | 2 | Reserved | Reserved | Reserved
87 | NCD Error Hrs | Hour | Unsigned Long Integer | 4 | 0.1 | Input Register | 163-164 | 2 |  | <Unavailable in Example Data/Image Above> | <Unavailable in Example Data/Image Above>
88 | NCD Heal Hrs | Hour | Unsigned Long Integer | 4 | 0.1 | Input Register | 165-166 | 2 |  | <Unavailable in Example Data/Image Above> | <Unavailable in Example Data/Image Above>
INPUT STATUS (Alarm)
1 | Fire/Smoke | NA | BIT | NA | NA | Input Status | 1 | 1 |  | 0 | Fire/Smoke Fault Absent
2 | Canopy Door Open | NA | BIT | NA | NA | Input Status | 2 | 1 |  | 0 | Canopy Door Open Fault Absent
3 | Load on Generator | NA | BIT | NA | NA | Input Status | 3 | 1 |  | 1 | Load on Generator
4 | Generator Fail to Start | NA | BIT | NA | NA | Input Status | 4 | 1 |  | 0 | Generator Fail to Start Fault Absent
5 | Generator Fail to Stop | NA | BIT | NA | NA | Input Status | 5 | 1 |  | 0 | Generator Fail to Stop Fault Absent
6 | Generator Common Fault | NA | BIT | NA | NA | Input Status | 6 | 1 |  | 0 | Generator Common Fault Absent
7 | Generator LLOP Fault | NA | BIT | NA | NA | Input Status | 7 | 1 |  | 0 | Generator LLOP Fault Absent
8 | Alternator Fault | NA | BIT | NA | NA | Input Status | 8 | 1 | Always 0 (Not populated) | 0 | (Not Supported)
9 | Low Fuel Level @ 15% | NA | BIT | NA | NA | Input Status | 9 | 1 |  | 0 | Low Fuel Level Fault Absent
10 | Canopy Temp High | NA | BIT | NA | NA | Input Status | 10 | 1 |  | 0 | Canopy Temp High Fault Absent
11 | Engine Coolant Temperature High | NA | BIT | NA | NA | Input Status | 11 | 1 |  | 0 | Engine Coolant Temperature High Fault Absent
12 | Fuel Temperature High | NA | BIT | NA | NA | Input Status | 12 | 1 | Always 0 (Not populated) | 0 | (Not Supported)
13 | Exhaust Temperature High | NA | BIT | NA | NA | Input Status | 13 | 1 | Always 0 (Not populated) | 0 | (Not Supported)
14 | Catalyst Converter Temperature High | NA | BIT | NA | NA | Input Status | 14 | 1 | Always 0 (Not populated) | 0 | (Not Supported)
15 | DG IDLE RUN | NA | BIT | NA | NA | Input Status | 15 | 1 |  | 0 | DG IDLE RUN Fault Absent
16 | DG Overload | NA | BIT | NA | NA | Input Status | 16 | 1 |  | 0 | DG Overload Fault Absent
17 | DG Battery Low | NA | BIT | NA | NA | Input Status | 17 | 1 |  | 0 | DG Battery Low Fault Absent
18 | Water in fuel alarm | NA | BIT | NA | NA | Input Status | 18 | 1 | Always 0 (Not populated) | 0 | (Not Supported)
19 | Water seepage alarm | NA | BIT | NA | NA | Input Status | 19 | 1 | Always 0 (Not populated) | 0 | (Not Supported)
20 | HT Ignition Coil open alarm | NA | BIT | NA | NA | Input Status | 20 | 1 | Always 0 (Not populated) | 0 | (Not Supported)
21 | Spark plug Faulty alarm | NA | BIT | NA | NA | Input Status | 21 | 1 | Always 0 (Not populated) | 0 | (Not Supported)
22 | Air filter choke alarm | NA | BIT | NA | NA | Input Status | 22 | 1 | Always 0 (Not populated) | 0 | (Not Supported)
23 | Gas Filter Choke Alarm | NA | BIT | NA | NA | Input Status | 23 | 1 | Always 0 (Not populated) | 0 | (Not Supported)
24 | Engine Coolant Level Low | NA | BIT | NA | NA | Input Status | 24 | 1 | Always 0 (Not populated) | 0 | (Not Supported)
25 | Gas Leakage Alarm | NA | BIT | NA | NA | Input Status | 25 | 1 | Always 0 (Not populated) | 0 | (Not Supported)
26 | System Shutdown due to Gas leakage | NA | BIT | NA | NA | Input Status | 26 | 1 | Always 0 (Not populated) | 0 | (Not Supported)
27 | Inginition Coil Lead disconnection alarm | NA | BIT | NA | NA | Input Status | 27 | 1 | Always 0 (Not populated) | 0 | (Not Supported)
28 | Generator Maintenance Alarm 50Hrs | NA | BIT | NA | NA | Input Status | 28 | 1 |  | 0 | Generator Maintenance Alarm 50Hrs Absent
29 | Generator Maintenance Alarm 100Hrs | NA | BIT | NA | NA | Input Status | 29 | 1 |  | 0 | Generator Maintenance Alarm 100Hrs Absent
30 | Generator Maintenance Alarm 500Hrs | NA | BIT | NA | NA | Input Status | 30 | 1 |  | 0 | Generator Maintenance Alarm 500Hrs Absent
31 | Generator Maintenance Alarm 1000Hrs | NA | BIT | NA | NA | Input Status | 31 | 1 |  | 0 | Generator Maintenance Alarm 1000Hrs Absent
32 | Generator Maintenance Alarm 2000Hrs | NA | BIT | NA | NA | Input Status | 32 | 1 |  | 0 | Generator Maintenance Alarm 2000Hrs Absent
33 | Low gas pressure at Pilot Regulator output alarm | NA | BIT | NA | NA | Input Status | 33 | 1 | Always 0 (Not populated) | 0 | (Not Supported)
34 | High gas pressure at Pilot Regulator output alarm | NA | BIT | NA | NA | Input Status | 34 | 1 | Always 0 (Not populated) | 0 | (Not Supported)
35 | Vibration sensor ON | NA | BIT | NA | NA | Input Status | 35 | 1 | Always 0 (Not populated) | 0 | (Not Supported)
36 | Radiator Water Level Low | NA | BIT | NA | NA | Input Status | 36 | 1 | Always 0 (Not populated) | 0 | (Not Supported)
37 | Engine Controller Fail alarm | NA | BIT | NA | NA | Input Status | 37 | 1 | Always 0 (Not populated) | 0 | (Not Supported)
38 | Main Controller Fail alarm | NA | BIT | NA | NA | Input Status | 38 | 1 |  | 0 | Main Controller Fail alarm Absent
39 | AVR fail alarm | NA | BIT | NA | NA | Input Status | 39 | 1 | Always 0 (Not populated) | 0 | (Not Supported)
40 | PFC Board Fail alarm | NA | BIT | NA | NA | Input Status | 40 | 1 | Always 0 (Not populated) | 0 | (Not Supported)
41 | AVR Excitation Voltage High | NA | BIT | NA | NA | Input Status | 41 | 1 | Always 0 (Not populated) | 0 | (Not Supported)
42 | Over Speed alarm | NA | BIT | NA | NA | Input Status | 42 | 1 |  | 0 | Over Speed alarm Absent
43 | Fuel Meter sensing high Consumption than CPH | NA | BIT | NA | NA | Input Status | 43 | 1 | Always 0 (Not populated) | 0 | (Not Supported)
44 | Fuel meter Tamper | NA | BIT | NA | NA | Input Status | 44 | 1 | Always 0 (Not populated) | 0 | (Not Supported)
45 | LLOP Tamper | NA | BIT | NA | NA | Input Status | 45 | 1 | Always 0 (Not populated) | 0 | (Not Supported)
46 | DG Run but no vibration alarm | NA | BIT | NA | NA | Input Status | 46 | 1 | Always 0 (Not populated) | 0 | (Not Supported)
47 | Reserved |  | BIT | NA | NA | Input Status | 47 | 1 | Reserved | 0 | Reserved
48 | EGR Warning | NA | BIT | NA | NA | Input Status | 48 | 1 |  | 0 | EGR Warning Absent
49 | EGR Fault | NA | BIT | NA | NA | Input Status | 49 | 1 |  | 1 | EGR Fault Present
50 | NCD Warning | NA | BIT | NA | NA | Input Status | 50 | 1 |  | <Unavailable in Example Data/Image Above> | <Unavailable in Example Data/Image Above>
51 | NCD Fault | NA | BIT | NA | NA | Input Status | 51 | 1 |  | <Unavailable in Example Data/Image Above> | <Unavailable in Example Data/Image Above>
52 | EGR ECU Unhealthy | NA | BIT | NA | NA | Input Status | 52 | 1 |  | <Unavailable in Example Data/Image Above> | <Unavailable in Example Data/Image Above>
53 | EGR Temperature Sensor Open Warning | NA | BIT | NA | NA | Input Status | 53 | 1 |  | <Unavailable in Example Data/Image Above> | <Unavailable in Example Data/Image Above>
54 | EGR Temperature Sensor Faulty Warning | NA | BIT | NA | NA | Input Status | 54 | 1 |  | <Unavailable in Example Data/Image Above> | <Unavailable in Example Data/Image Above>
55 | EGR Valve Open Warning | NA | BIT | NA | NA | Input Status | 55 | 1 |  | <Unavailable in Example Data/Image Above> | <Unavailable in Example Data/Image Above>
56 | EGR Valve Sensor Faulty Warning | NA | BIT | NA | NA | Input Status | 56 | 1 |  | <Unavailable in Example Data/Image Above> | <Unavailable in Example Data/Image Above>
57 | EGR Valve Not Lifting Warning | NA | BIT | NA | NA | Input Status | 57 | 1 |  | <Unavailable in Example Data/Image Above> | <Unavailable in Example Data/Image Above>
58 | EGR Valve Not Closing Warning | NA | BIT | NA | NA | Input Status | 58 | 1 |  | <Unavailable in Example Data/Image Above> | <Unavailable in Example Data/Image Above>
COIL STATUS
1 | DG STOP Command / DG OFF | NA | BIT | NA | NA | Coil Status | 1 | 1 |  | 0 | DG On
2 | DG START Command / DG ON | NA | BIT | NA | NA | Coil Status | 2 | 1 |  | 1 | DG On
3 | Remote Mode | NA | BIT | NA | NA | Coil Status | 3 | 1 |  | 0 | Remote Mode Disabled
4 | Manual Mode | NA | BIT | NA | NA | Coil Status | 4 | 1 |  | 1 | Manual Mode Enabled
5 | Future Use | NA | BIT | NA | NA | Coil Status | 5 | 1
6 | Future Use | NA | BIT | NA | NA | Coil Status | 6 | 1
7 | Future Use | NA | BIT | NA | NA | Coil Status | 7 | 1
8 | Future Use | NA | BIT | NA | NA | Coil Status | 8 | 1
9 | Future Use | NA | BIT | NA | NA | Coil Status | 9 | 1
HOLDING REGISTER
1 | DG OP Voltage Low cutoff | Volt | Unsigned Integer | 2 | 1 | Holding Register | 1 | 1 |  | 185 | 185 V
2 | DG OP Voltage High cutoff | Volt | Unsigned Integer | 2 | 1 | Holding Register | 2 | 1 |  | 285 | 285V
3 | DG start first crank set | Seconds | Unsigned Integer | 2 | 1 | Holding Register | 3 | 1 |  | 2 | 2 seconds
4 | DG start second crank set | Seconds | Unsigned Integer | 2 | 1 | Holding Register | 4 | 1 | Always 0xffff (Unused) | -1 | (Not Supported)
5 | DG start third crank set | Seconds | Unsigned Integer | 2 | 1 | Holding Register | 5 | 1 | Always 0xffff (Unused) | -1 | (Not Supported)
6 | Rest after first Crank | Seconds | Unsigned Integer | 2 | 1 | Holding Register | 6 | 1 |  | 10 | 10 seconds
7 | Rest after second Crank | Seconds | Unsigned Integer | 2 | 1 | Holding Register | 7 | 1 | Always 0xffff (Unused) | -1 | (Not Supported)
8 | DG Overload Trip | Seconds | Unsigned Integer | 2 | 1 | Holding Register | 8 | 1 |  | 15 | 15 seconds

## USB (For Internal Usage) (hidden)
Note: THIS SHEET IS CONFIDENTIAL. USB PROTOCOL DETAILS NOT TO BE SHARED WITH CUSTOMER. ADDITIONALLY SOME FIELDS ON MODBUS ARE PROCOM SPECIFIC.
Sn. | Function | Function Code | Type | Units of | Data Type | Size in byte | Data Format | Write Restrictions | Return Code | Remarks | Visibility
|  |  |  | Measurement | (Float/Hex etc.)
1 | Update Settings | 0x90 | Write | NA | Byte Array | Large |  |  | No response on Success, else failure |  | Visible To Customer
2 | Read Settings | 0x92 | Read | NA | Byte Array | Large |  |  | 0 on success else failure |  | Visible To Customer
3 | Read Instant Parameters | 0x93 | Read | NA | Byte Array | Large |  |  | 0 on success else failure |  | Visible To Customer
4 | Set RTC | 0x94 | Write | NA | BCD | 8 |  |  | 0z91 on success else failure |  | Visible To Customer
5 | Read RTC | 0x95 | Read | NA | BCD | 8 |  | Should be a proper date/time format | 0x95 on success else failure | Should always be set by Production Team with correct date/time | Visible To Customer
6 | Read Fault Recordings | 0x96 | Read | NA | Byte Array | Variable |  |  | 0 on success else failure |  | Visible To Customer
7 | Read Event Recordings | 0x97 | Read | NA | Byte Array | Variable |  |  | 0 on success else failure |  | Visible To Customer
8 | Read Start Stop Recordings | 0x98 | Read | NA | Byte Array | Variable |  |  | 0 on success else failure |  | Visible To Customer
9 | Reset Service Hours | 0x99 | Write | NA | NA | 0 |  |  | 0z91 on success else failure |  | Visible To Customer
10 | Set Password | 0x9B | Write | NA | Byte | 1 | Integer of 1 byte size | Valid value is an integer between 1-999 | 0x9B on success else failure |  | Visible To Customer
11 | Read Instant Store Recordings | 0x9C | Read | NA | Byte Array | Variable | Same as Fault Recordings (But see INSTANT_STORE instead of ENTRY_STORE) |  | 0 on success else failure |  | Visible To Customer
12 | Read Energy Store Recordings | 0x9D | Read | NA | Byte Array | Variable | Same as Fault Recordings (But see ENERGY_STORE instead of ENTRY_STORE) |  | 0 on success else failure |  | Visible To Customer
13 | Read Genset Serial Number | 0x9E | Read | NA | ASCII String (null terminated) | 20 | String of max 19 characters + 1 Null terminator. All strings are null-terminated |  | 0x9E on success else failure |  | Visible To Customer
14 | Set Genset Serial Number | 0x9F | Write | NA | ASCII String (null terminated) | 20 | String of max 19 characters + 1 Null terminator. All strings are null-terminated | Max length is 19 characters | 0z91 on success else failure |  | Visible To Customer
15 | Read Engine Serial Number | 0xA0 | Read | NA | ASCII String (null terminated) | 20 | String of max 19 characters + 1 Null terminator. All strings are null-terminated |  | 0xA0 on success else failure | Initially all zero till it's set by customer. | Visible To Customer
16 | Set Engine Serial Number | 0xA1 | Write | NA | ASCII String (null terminated) | 20 | String of max 19 characters + 1 Null terminator. All strings are null-terminated | Max length is 19 characters | 0z91 on success else failure |  | Visible To Customer
17 | Read Alternator Serial Number | 0xA2 | Read | NA | ASCII String (null terminated) | 20 | String of max 19 characters + 1 Null terminator. All strings are null-terminated |  | 0xA2 on success else failure | Initially all zero till it's set by customer. | Visible To Customer
18 | Set Alternator Serial Number | 0xA3 | Write | NA | ASCII String (null terminated) | 20 | String of max 19 characters + 1 Null terminator. All strings are null-terminated | Max length is 19 characters | 0z91 on success else failure |  | Visible To Customer
19 | Read Engine Controller Serial Number | 0xA4 | Read | NA | ASCII String (null terminated) | 20 | String of max 19 characters + 1 Null terminator. All strings are null-terminated |  | 0xA4 on success else failure | Initially all zero till it's set by customer. | Visible To Customer
20 | Set Engine Controller Serial Number | 0xA5 | Write | NA | ASCII String (null terminated) | 20 | String of max 19 characters + 1 Null terminator. All strings are null-terminated | Max length is 19 characters | 0z91 on success else failure |  | Visible To Customer
21 | Read Product Rating | 0xA6 | Read | KVA | Unsigned Integer | 4 | Non-zero integer with max 3 digit |  | 0xA6 on success else failure |  | Visible To Customer
22 | Set Product Rating | 0xA7 | Write | KVA | Unsigned Integer | 4 | Non-zero integer with max 3 digit | Valid value is an integer between 1-999 | 0z91 on success else failure |  | Visible To Customer
23 | Read Comissioning Date+Time | 0xA8 | Read | NA | BCD | 8 | Same as RTC |  | 0xA8 on success else failure | Initially all zero till it's set by customer. | Visible To Customer
24 | Set Comissioning Date+Time | 0xA9 | Write | NA | BCD | 8 | Same as RTC | Should be a valid date-time format | 0z91 on success else failure |  | Visible To Customer
Product/Version Identification (Common across all new controllers)
25 | Set Site Id | 0x43 | Write | NA | ASCII String (null terminated) | 10 | String of max 9 characters + 1 Null terminator. All strings are null-terminated | Max length is 19 characters | 0z91 on success else failure |  | Visible To Customer
26 | Set Controller Serial Number | 0x44 | Write | NA | ASCII String (null terminated) | 20 | String of max 19 characters + 1 Null terminator. All strings are null-terminated | Should be unique for each controller. Max length is 19 characters. | 0z91 on success else failure | Should always be set by production team before sending to customer. | Not visible to customer. Only visible to Production team.
27 | Read Product Name | 0x16 | Read | NA | ASCII String (null terminated) | 20 | String of max 19 characters + 1 Null terminator. All strings are null-terminated |  | 0x16 on success else failure | Always "ECON-MAN-INDUS". Helps identify controller type. | Visible To Customer
28 | Read Product Version | 0x17 | Read | NA | ASCII String (null terminated) | 20 | String of max 19 characters + 1 Null terminator. All strings are null-terminated |  | 0x17 on success else failure | Always of format "v<MajorVersion>.<MinorVersion>". Helps identify controller version | Visible To Customer
29 | Read Site Id | 0x18 | Read | NA | ASCII String (null terminated) | 20 | String of max 19 characters + 1 Null terminator. All strings are null-terminated |  | 0x18 on success else failure | Initially all zero till it's set by customer. | Visible To Customer
30 | Read Serial Number | 0x19 | Read | NA | ASCII String (null terminated) | 20 | String of max 19 characters + 1 Null terminator. All strings are null-terminated |  | 0x19 on success else failure | Initially all zero till it's set by production team. | Visible To Customer

## Settings (hidden)
Controller: | ECON-MAN-IND
Firmware | v2.04/v2.06
No. | Name Of Setting On LCD Display | Setting Description | Default setting | Setting Range | Edit Options
1 | Suppliers | Company logo and default parameter is set as per system suppliers. | Procom | PROCOM TMTL M&M | Only Settable via Windows Software
2 | System Conﬁg | ECON provides complete ﬂexibility in system designing; it is possible to select manual operation for DG phases. | Generator 3 Phase | Generator 1 Phase Generator 3 Phase | Settable via Keypad on Controller or Windows Software
3 | Solenoid Type | Pull To Start In this mode fuel solenoid contact changes from Open to Close at the time of cranking and remains close till the gen set is running. For stopping the generator this contact opens. Pull To Stop In this mode fuel solenoid contact remains open at the time of cranking and till the gen set is running. For stopping the generator this contact closes for a user programmed time. | Pull To Stop | Pull to Stop Pull to Start | Only Settable via Windows Software
4 | LLOP Sensor Type | Select the installed sensor for LLOP | TMTL | User Deﬁned Type A M&M MNEPL VE TMTL HUAFANG TATA GC(VDO) GC(MURPHY) 4-20MA M&M-2 Disabled * | Only Settable via Windows Software
5 | LLOP Sensor R1 | R1 to R10 = Resistance Value V1 to V10 = Corresponding pressure value. These table are used when sensor type is selected as user deﬁned. | 10Ω | 0-999Ω | Only Settable via Windows Software
6 | LLOP Sensor V1 |  | 0 Bar | 0.0-10.0 Bar | Only Settable via Windows Software
7 | LLOP Sensor R2 |  | 29Ω | 0-999Ω | Only Settable via Windows Software
8 | LLOP Sensor V2 |  | 1 Bar | 0.0-10.0 Bar | Only Settable via Windows Software
9 | LLOP Sensor R3 |  | 38Ω | 0-999Ω | Only Settable via Windows Software
10 | LLOP Sensor V3 |  | 1.5Bar | 0.0-10.0 Bar | Only Settable via Windows Software
11 | LLOP Sensor R4 |  | 48Ω | 0-999Ω | Only Settable via Windows Software
12 | LLOP Sensor V4 |  | 2Bar | 0.0-10.0 Bar | Only Settable via Windows Software
13 | LLOP Sensor R5 |  | 57Ω | 0-999Ω | Only Settable via Windows Software
14 | LLOP Sensor V5 |  | 2.5Bar | 0.0-10.0 Bar | Only Settable via Windows Software
15 | LLOP Sensor R6 |  | 67Ω | 0-999Ω | Only Settable via Windows Software
16 | LLOP Sensor V6 |  | 3Bar | 0.0-10.0 Bar | Only Settable via Windows Software
17 | LLOP Sensor R7 |  | 86Ω | 0-999Ω | Only Settable via Windows Software
18 | LLOP Sensor V7 |  | 4Bar | 0.0-10.0 Bar | Only Settable via Windows Software
19 | LLOP Sensor R8 |  | 105Ω | 0-999Ω | Only Settable via Windows Software
20 | LLOP Sensor V8 |  | 5Bar | 0.0-10.0 Bar | Only Settable via Windows Software
21 | LLOP Sensor R9 |  | 124Ω | 0-999Ω | Only Settable via Windows Software
22 | LLOP Sensor V9 |  | 6Bar | 0.0-10.0 Bar | Only Settable via Windows Software
23 | LLOP Sensor R10 |  | 143Ω | 0-999Ω | Only Settable via Windows Software
24 | LLOP Sensor V10 |  | 7Bar | 0.0-10.0 Bar | Only Settable via Windows Software
25 | Fuel Sensor | Select the installed sensor for Fuel The installed sensor should be Electronics or Linear if system suppliers as TMTL | .5-4.5(0-100%) | User Deﬁned Type A Sam-0 Sam-1 Electronics Linear 0-5V(0-100%) Disabled* | Only Settable via Windows Software
26 | Fuel Sensor R1 | R1 to R10 = Resistance Value V1 to V10 = Corresponding fuel level in %. These table are used when sensor type is selected as user deﬁned. | 10Ω | 0-999Ω | Only Settable via Windows Software
27 | Fuel Sensor V1 |  | 0 | 0-100% | Only Settable via Windows Software
28 | Fuel Sensor R2 |  | 29Ω | 0-999Ω | Only Settable via Windows Software
29 | Fuel Sensor V2 |  | 0.1 | 0-100% | Only Settable via Windows Software
30 | Fuel Sensor R3 |  | 48Ω | 0-999Ω | Only Settable via Windows Software
31 | Fuel Sensor V3 |  | 0.2 | 0-100% | Only Settable via Windows Software
32 | Fuel Sensor R4 |  | 67Ω | 0-999Ω | Only Settable via Windows Software
33 | Fuel Sensor V4 |  | 0.3 | 0-100% | Only Settable via Windows Software
34 | Fuel Sensor R5 |  | 86Ω | 0-999Ω | Only Settable via Windows Software
35 | Fuel Sensor V5 |  | 0.4 | 0-100% | Only Settable via Windows Software
36 | Fuel Sensor R6 |  | 105Ω | 0-999Ω | Only Settable via Windows Software
37 | Fuel Sensor V6 |  | 0.5 | 0-100% | Only Settable via Windows Software
38 | Fuel Sensor R7 |  | 124Ω | 0-999Ω | Only Settable via Windows Software
39 | Fuel Sensor V7 |  | 0.6 | 0-100% | Only Settable via Windows Software
40 | Fuel Sensor R8 |  | 143Ω | 0-999Ω | Only Settable via Windows Software
41 | Fuel Sensor V8 |  | 0.7 | 0-100% | Only Settable via Windows Software
42 | Fuel Sensor R9 |  | 181Ω | 0-999Ω | Only Settable via Windows Software
43 | Fuel Sensor V9 |  | 0.9 | 0-100% | Only Settable via Windows Software
44 | Fuel Sensor R10 |  | 200Ω | 0-999Ω | Only Settable via Windows Software
45 | Fuel Sensor V10 |  | 100 | 0-100% | Only Settable via Windows Software
46 | Fuel Tank Capacity | The capacity of the fuel tank in litres. | 250 Ltr | Disabled 0-999Ltr | Only Settable via Windows Software
47 | HET Sensor | Select the installed sensor for HET The installed sensor should be either TMTL AIR 1C or TMTL AIR 3C or TMTL WATER if system suppliers as TMTL | TMTL Range 2 | User Deﬁned Type A M&M MNEPL VE TMTL RANGE 1 TMTL RANGE 2 TMTL WATER HUAFANG TATA GC(VDO) GC(MURPHY) Disabled * | Only Settable via Windows Software
48 | HET Sensor R1 | R1 to R10 = Resistance Value V1 to V10 = Corresponding temperature in °C. These table are used when sensor type is selected as user deﬁned. | 540Ω | 0-9999Ω | Only Settable via Windows Software
49 | HET Sensor V1 |  | 40℃ | 0-300 Celsius | Only Settable via Windows Software
50 | HET Sensor R2 |  | 458Ω | 0-9999Ω | Only Settable via Windows Software
51 | HET Sensor V2 |  | 45℃ | 0-300 Celsius | Only Settable via Windows Software
52 | HET Sensor R3 |  | 222Ω | 0-9999Ω | Only Settable via Windows Software
53 | HET Sensor V3 |  | 65℃ | 0-300 Celsius | Only Settable via Windows Software
54 | HET Sensor R4 |  | 120Ω | 0-9999Ω | Only Settable via Windows Software
55 | HET Sensor V4 |  | 85℃ | 0-300 Celsius | Only Settable via Windows Software
56 | HET Sensor R5 |  | 93Ω | 0-9999Ω | Only Settable via Windows Software
57 | HET Sensor V5 |  | 90℃ | 0-300 Celsius | Only Settable via Windows Software
58 | HET Sensor R6 |  | 80Ω | 0-9999Ω | Only Settable via Windows Software
59 | HET Sensor V6 |  | 95℃ | 0-300 Celsius | Only Settable via Windows Software
60 | HET Sensor R7 |  | 70Ω | 0-9999Ω | Only Settable via Windows Software
61 | HET Sensor V7 |  | 100℃ | 0-300 Celsius | Only Settable via Windows Software
62 | HET Sensor R8 |  | 60Ω | 0-9999Ω | Only Settable via Windows Software
63 | HET Sensor V8 |  | 105℃ | 0-300 Celsius | Only Settable via Windows Software
64 | HET Sensor R9 |  | 53Ω | 0-9999Ω | Only Settable via Windows Software
65 | HET Sensor V9 |  | 110℃ | 0-300 Celsius | Only Settable via Windows Software
66 | HET Sensor R10 |  | 46Ω | 0-9999Ω | Only Settable via Windows Software
67 | HET Sensor V10 |  | 115℃ | 0-300 Celsius | Only Settable via Windows Software
68 | Sensor Open | User can select the action to be taken in case of sensor open, it can be configured as a fault, or as warning | Disabled | Disabled * Warning | Settable via Keypad on Controller or Windows Software
69 | CT Ratio | Current Transformer ratio | 1 | 1-100 | Only Settable via Windows Software
70 | Gen. RPM | Engine RPM Type | 1500 RPM | 1500RPM 3000RPM | Only Settable via Windows Software
71 | Contact ON Pin 32 | These are three programmable output which can be configured for any one function from the list | Heater/choke | None Unit Healthy Load Warning Fuel Pump Heater /Choke Pull Solenoid | Only Settable via Windows Software
72 | Contact ON Pin 31 | These are three programmable output which can be conﬁgured for any one function from the list | None | None Unit Healthy Load Warning Fuel Pump Heater /Choke Pull Solenoid | Settable via Keypad on Controller or Windows Software
73 | Contact ON Pin 30 | These are three programmable output which can be conﬁgured for any one function from the list | None | None Unit Healthy Load Warning Fuel Pump Heater / Choke Pull Solenoid | Settable via Keypad on Controller or Windows Software
74 | Over Load KW | The Power(KW) above which the over load fault monitoring will start. The timer for it is over load delay. This fault is only enabled while the generator is running. On expiry of the timer the generator is stopped | 9.2 KW | 1.0-20.0 KW | Only Settable via Windows Software
75 | Over Current | The current above which the over current fault monitoring will start. The timer for it is over load delay. This fault is only enabled while the generator is running. On expiry of thetimer the generator is stopped | 50.1 A | 1.0-150 A | Only Settable via Windows Software
76 | Over Load Delay | This is the timer for the over load condition either due to over KW or over current. On expiry of this timer the engine shall be stopped | 10 Sec | 1-15 Sec | Only Settable via Windows Software
77 | High load KW | The Power(KW) above which the High load fault monitoring will start. The timer for it is High load delay. This fault is only enabled while the generator is running. On expiry of the timer the generator is stopped | Disabled | Disabled* 1.0-20KW | Only Settable via Windows Software
78 | High delay | This is the timer for the High load Condition. On expiry of this timer the engine shall be stopped | 10 Sec | 1-9999Sec | Only Settable via Windows Software
79 | Reverse power | The Power(KW) above which the Res. Power fault monitoring will start. The timer for it is Res. Power delay. This fault is only enabled while the generator is running. On expiry of the timer the generator is stopped | Disabled | Disable* 0.5-150 KW | Settable via Keypad on Controller or Windows Software
80 | Reverse power delay | This is the timer for the Res. Power Condition. On expiry of this timer the engine shall be stopped | 10 Sec | 1-999 Sec | Settable via Keypad on Controller or Windows Software
81 | Digital Input 1 | This can be conﬁgured for one out the listed below Parameters. RWL Oil Level Oil Temperature Canopy Temperature | RWL | RWL Oil Level Oil Temp. Canopy Temp. | Settable via Keypad on Controller or Windows Software
82 | Digital Input 1 Polarity | The polarity of digital input can be changed either normally open or normally close. | Normally open | Normally Open Normally Close | Settable via Keypad on Controller or Windows Software
83 | Digital Input 2 | This can be configured for one out the listed below Parameters. LLOP Oil Level Oil Temperature Canopy Temperature | LLOP | LLOP Oil Level Oil Temp. Canopy Temp. | Settable via Keypad on Controller or Windows Software
84 | Digital Input 2 Polarity | The polarity of digital input can be changed either normally open or normally close. | Normally open | Normally Open Normally Close | Settable via Keypad on Controller or Windows Software
85 | Digital Input 3 | This can be configured for one out the listed below Parameters. Low Fuel Oil Level, Oil Temperature Canopy Temperature | Low Fuel | Low Fuel Oil Level Oil Temp. Canopy Temp. | Only Settable via Windows Software
86 | Digital Input 3 Polarity | The polarity of digital input can be changed either normally open or normally close. | Normally open | Normally Open Normally Close | Only Settable via Windows Software
87 | Digital Input 4 | This can be configured for one out the listed below Parameters. HET Oil Level Oil Temperature Canopy Temperature | HET/HWT | HET/HWT Oil Level Oil Temp. Canopy Temp. | Settable via Keypad on Controller or Windows Software
88 | Digital Input 4 Polarity | The polarity of digital input can be changed either normally open or normally close. | Normally open | Normally Open Normally Close | Settable via Keypad on Controller or Windows Software
89 | Digital Input 5 | This can be configured for one of the listed below Parameters. Canopy door open Oil Level Oil Temperature Canopy Temperature V- belt Ext-1 Ext-2 EGR Warning EGR Fault Padmini EGR | C Door open | C Door open V-belt Ext-1, Ext-2 EGR Warning EGR Fault Padmini EGR | Settable via Keypad on Controller or Windows Software
90 | Digital Input 5 Polarity | The polarity of digital input can be changed either normally open or normally close. | Normally open | Normally Open Normally Close | Settable via Keypad on Controller or Windows Software
91 | Digital Input 6 | This can be configured for one of the listed below Parameters. Fire Oil Level Oil Temperature Canopy Temperature V- belt Ext-1 Ext-2 EGR Warning EGR Fault Padmini EGR | Fire | Fire Oil Level Oil Temp. Canopy Temp. V-belt Ext-1, Ext-2 EGR Warning EGR Fault Padmini EGR | Settable via Keypad on Controller or Windows Software
92 | Digital Input 6 Polarity | The polarity of digital input can be changed either normally open or normally close. | Normally open | Normally Open Normally Close | Settable via Keypad on Controller or Windows Software
93 | Digital Input 7 | This can be configured for one of the listed below Parameters. Half Fuel Warning Oil Level Oil Temperature Canopy Temperature V- belt Ext-1 Ext-2 EGR Warning EGR Fault Padmini EGR | Half Fuel Warning | Half Fuel Warning Oil Level Oil Temp. Canopy Temp. V-belt Ext-1, Ext-2 EGR Warning EGR Fault Padmini EGR | Only Settable via Windows Software
94 | Digital Input 7 Polarity | The polarity of digital input can be changed either normally open or normally close. | Normally open | Normally Open Normally Close | Only Settable via Windows Software
95 | Digital Input 8 | This can be conﬁgured for one of the listed below Parameters. Oil Level Oil Temperature Canopy Temperature V-belt Ext-1 Ext-2 EGR Warning EGR Fault Padmini EGR | Canopy Temp. | Oil Level Oil Temp. Canopy Temp. V-belt Ext-1, Ext-2 EGR Warning EGR Fault Padmini EGR | Settable via Keypad on Controller or Windows Software
96 | Digital Input 8 Polarity | The polarity of digital input can be changed either normally open or normally close. | Normally open | Normally Open Normally Close | Settable via Keypad on Controller or Windows Software
97 | Fan high current | Maximum limit for fan | 1.1A | Disable* 0-3.5A | Only Settable via Windows Software
98 | Fan low current | Minimum Limit For fan current. This Parameter is disabled if the above paramters is disabled. | 0.2A | 0-3.5A | Only Settable via Windows Software
99 | Fan current delay | This is the timer for fan current trip. | 15 Sec | 1-60 Sec | Only Settable via Windows Software
100 | Generator O/V | Max. Permissible Generator voltage, above this the Generator voltage is treated unhealthy & the Generator is stopped on voltage fault. | 285V | 150-300V | Only Settable via Windows Software
101 | Generator U/V | Min. permissible Generator voltage, below this the Generator voltage is treated unhealthy & the Generator is stopped on voltage fault. | 185V | 100-200V | Only Settable via Windows Software
102 | Gen Voltage Delay | Duration for which generator Over/Under voltage condition can be tolerated before stopping the Generator. | 10 Sec | 1-300 Sec | Only Settable via Windows Software
103 | Generator Over Frq. | Max. Permissible Generator Frq., above this the Generator Frq. is treated unhealthy & the Generator is stopped on Frq. fault. | 55 Hz | 25-70Hz Disable* | Only Settable via Windows Software
104 | Generator Under Frq. | Min. permissible Generator Frq., below this the Generator Frq. is treated unhealthy & the Generator isstopped Frq. fault. | 45 Hz | Disable* 25-70Hz | Only Settable via Windows Software
105 | Gen Frq. Delay | Duration for which Generator Over /Under Frq. condition can be tolerated before stopping the Generator. This setting is not available if (4)&(5) are disabled | 5 sec | 1-300 Sec. | Only Settable via Windows Software
106 | Current Unbalance | The maximum permissible current unbalance in %. The unbalance starts only after the system is loaded to 25%of its capacity | Disabled | 5-100% Disable | Only Settable via Windows Software
107 | Current Unbalance Delay | Duration for which the current unbalance can be tolerated before triggering the fault | 10 Sec | 1-999Sec | Only Settable via Windows Software
108 | Pickup Voltage | This parameter speciﬁes the generator voltage at which it is presumed to have started and crank has to be terminated | 30V | 30-150V | Only Settable via Windows Software
109 | Pick Up RPM | This parameter speciﬁes the edge RPM ( deﬁne for DG voltage) at which crank shall be terminated. | 300RPM | 300-1200 | Only Settable via Windows Software
110 | First Service Due Hr | Time, in hours, for next service due warning. | 500 | 1-999 Hrs | Settable via Keypad on Controller or Windows Software
111 | Later service due hr | Time, in hours, for next service due warning. | 500 | 1-999 Hrs | Settable via Keypad on Controller or Windows Software
112 | Crank Cut Method | Auto disconnects the crank command on detection of either voltage build-up/ voltage or oil pressure build up | Volt+Hz+Switch | Volt+Hz Volt+Hz+Switch Volt+Hz+Sensor Volt+Hz+Sensor+Switch | Only Settable via Windows Software
113 | Pick Up KVA | If the current level crosses this limit the contact is energized after the programmed supervision time | 8 KVA | 1-9999 KVA | Only Settable via Windows Software
114 | Reset KVA | If the current level falls below this limit the contact is de-energized after the programmed supervision time. | 8 KVA | 1-9999 KVA | Only Settable via Windows Software
115 | KVA Warning Delay | The supervision time for the above 2 parameters. | 5 Sec | 1-999 Sec | Only Settable via Windows Software
116 | Choke Pre time | Keep the choke for this time before the engine has started. | Disabled | Disable* 1-999 Sec | Settable via Keypad on Controller or Windows Software
117 | Choke Post time | Keep the choke for this time after the engine has started. | Disabled | Disable* 1-999 Sec | Settable via Keypad on Controller or Windows Software
118 | Pump Pre Time | Activate the Pump by this time before cranking | 2 Sec | 1-999Sec | Only Settable via Windows Software
119 | Generator Warmup Delay | The load is switched to Generator after expiry of this time | 0 Sec | 0-999Sec | Settable via Keypad on Controller or Windows Software
120 | Generator Recooling Delay | The time for which the Generator is allowed to run on no load before switching off | 30 Sec | 0-999Sec | Settable via Keypad on Controller or Windows Software
121 | Fuel Warn Level | Monitoring value of fuel level below which fuel level warning is generated. | 50% | Disable* 10-80 % | Only Settable via Windows Software
122 | Fuel Warn Delay | Monitoring time of fuel level after which fuel level warning is generated. | 10 Sec | 1-99 Sec | Only Settable via Windows Software
123 | Fuel Trip Level | Monitoring value of fuel level below which fuel level trip is generated. | 15% | 10-81 % Disable | Only Settable via Windows Software
124 | Fuel Trip Delay | Monitoring time of fuel level after which fuel level trip is generated. | 10 Sec | 1-999 Sec | Only Settable via Windows Software
125 | LLOP Trip Level | Monitoring value of lube oil pressure below which LLOP trip is generated. | 0.7 Kg/Cm2 | 0.3-8.5 Kg/cm2 Disable | Only Settable via Windows Software
126 | LLOP Trip Delay | Monitoring time of lube oil pressure after which LLOP trip is generated. | 10 Sec | 0-999 Sec | Only Settable via Windows Software
127 | HET Trip Level | Monitoring value of water temperature above which HET trip is generated. | Disabled | 40-251 Disabled* | Only Settable via Windows Software
128 | HET Trip Delay | Monitoring time of water temperature after which HET trip is generated. | 10 Sec | 10-60 Sec | Only Settable via Windows Software
129 | Digital Input 1 Delay | Delay for programmable digital input. Digital input are explained above. | 10 Sec | 1-99 Sec | Settable via Keypad on Controller or Windows Software
130 | Digital Input 2 Delay | Delay for programmable digital input. Digital input are explained above. | 10 Sec | 1-99 Sec | Settable via Keypad on Controller or Windows Software
131 | Digital Input 3 Delay | Delay for programmable digital input. Digital input are explained above. | 10 Sec | 1-99 Sec | Only Settable via Windows Software
132 | Digital Input 4 Delay | Delay for programmable digital input. Digital input are explained above. | 10 Sec | 1-99 Sec | Settable via Keypad on Controller or Windows Software
133 | Digital Input 5 Delay | Delay for programmable digital input. Digital input are explained above. | 10 Sec | 1-99 Sec | Settable via Keypad on Controller or Windows Software
134 | Digital Input 6 Delay | Delay for programmable digital input. Digital input are explained above. | 10 Sec | 1-99 Sec | Settable via Keypad on Controller or Windows Software
135 | Digital Input 7 Delay | Delay for programmable digital input. Digital input are explained above. | 10 Sec | 1-99 Sec | Only Settable via Windows Software
136 | Digital Input 8 Delay | Delay for programmable digital input. Digital input are explained above. | 10 Sec | 1-99 Sec | Settable via Keypad on Controller or Windows Software
137 | Chg Alt-V Belt Delay | Duration for which the V-Belt signal should be continuously deactive to be recognized as a fault and action initiated. This fault is only enabled while the generator is running. | 180 Sec | Disable* 1-299 Sec | Settable via Keypad on Controller or Windows Software
138 | Hooter ON Time | Duration for which the hooter shall be ON, if not externally reset, while announcing a fault. | 30 Sec | 1-299 Sec | Settable via Keypad on Controller or Windows Software
139 | Crank ON Time | Maximum crank time | 2.0 Sec | 0.5-5 Sec | Settable via Keypad on Controller or Windows Software
140 | Crank Gap Time | The delay between two successive cranks | 10 Sec | 1-99 Sec | Settable via Keypad on Controller or Windows Software
141 | Crank Attempts | The maximum number of cranks that shall be issued to start the Engine | 3 | 3-5 | Settable via Keypad on Controller or Windows Software
142 | Solenoid ON time | The time for which stop solenoid will be kept active while stopping the engine | 35 Sec | 1-99 Sec | Settable via Keypad on Controller or Windows Software
143 | Disp Auto Scroll | Setting ON will enable Auto Scroll of display. OFF: No scroll and next parameter can be viewed by pressing next switch | ON | ON/OFF | Settable via Keypad on Controller or Windows Software
144 | Scrolling Delay | After this duration next parameter Displayed on Display. | 10 Sec | 5-99Sec | Settable via Keypad on Controller or Windows Software
145 | Battery UV Warning | Min. permissible battery voltage, below this the voltage is treated unhealthy & warning is generated. | 10.0 V | Disabled* 7.9-12V | Settable via Keypad on Controller or Windows Software
146 | Battery OV Warning | Max. permissible battery voltage, above this the voltage is treated unhealthy & warning is generated. | 14.5 V | 12-30V Disabled* | Settable via Keypad on Controller or Windows Software
147 | Canopy Over Temp. | Monitoring value of Canopy Temp. Above which Canopy temp. Is generated. | 27.0 Celsius | 15.0-99.9 Celsius | Settable via Keypad on Controller or Windows Software
148 | Canopy Over Temp. Delay | Monitoring Time value of Canopy Temp. After which Canopy temp. Is generated. | 20 sec | 1-999Sec | Settable via Keypad on Controller or Windows Software
149 | NCD Strategy | Enable or Disable NCD (NOx Control Diagnostic) System as per CPCB4+ guidelines | Disabled* | Disabled* 0.01-99.99Hrs | Settable via Keypad on Controller or Windows Software
150 | NCD Warn Hrs | Set the time in Hrs while Generator is running after which NCD Warning will get activated if any EGR warning remains in the system during this whole period. | 36.00 Hrs | 0.01-99.99 Hrs | Settable via Keypad on Controller or Windows Software
151 | NCD Fault Hrs | Set the time in Hrs while Generator is running after which NCD Fault will get activated if any EGR warning remains in the system during this whole period. | 72.00 Hrs | 0.01-99.99 Hrs | Settable via Keypad on Controller or Windows Software
152 | NCD Heal Hrs | Set the time in Hrs while Generator is running after which NCD Error timer will get reset if no EGR warning remains in the system during this whole period. | 40.00 Hrs | 0.01-99.99 Hrs | Settable via Keypad on Controller or Windows Software
153 | Ann. DG On | Selected contact is activated if Generator is on | No Annuciation | Disabled Contact on pin 1-12 | Settable via Keypad on Controller or Windows Software
154 | Ann. DG Off | Selected contact is activated if Generator is off. | No Annuciation | Disabled Contact on pin 1-12 | Settable via Keypad on Controller or Windows Software
155 | Ann. DG On Load | Selected contact is activated if Generator is On load | On Contact 7 | Disabled Contact on pin 1-12 | Settable via Keypad on Controller or Windows Software
156 | Ann. Unit OK | Selected contact is activated if unit is ok. | No Annuciation | Disabled Contact on pin 1-12 | Settable via Keypad on Controller or Windows Software
157 | Ann. Fuel Trip | Selected contact is activated if fuel fault registered | On Contact 10 | Disabled Contact on pin 1-12 | Settable via Keypad on Controller or Windows Software
158 | Ann. LLOP Trip | Selected contact is activated if LLOP fault registered | On Contact 1 | Disabled Contact on pin 1-12 | Settable via Keypad on Controller or Windows Software
159 | Ann. HET Trip | Selected contact is activated if HET fault registered. | On Contact 2 | Disabled Contact on pin 1-12 | Settable via Keypad on Controller or Windows Software
160 | Ann. DG Voltage | Selected contact is activated if Generator voltage is healthy. | No Annuciation | Disabled Contact on pin 1-12 | Settable via Keypad on Controller or Windows Software
161 | Ann. Emergency | Selected contact is activated if emergency fault is registered. | No Annuciation | Disabled Contact on pin 1-12 | Settable via Keypad on Controller or Windows Software
162 | Ann. DG Overload | Selected contact is activated if generator is overloaded. | On Contact 3 | Disabled Contact on pin 1-12 | Settable via Keypad on Controller or Windows Software
163 | Ann. DG High Load | Selected contact is activated if generator is highloaded. | No Annuciation | Disabled Contact on pin 1-12 | Settable via Keypad on Controller or Windows Software
164 | Ann. DG Frequency | Selected contact is activated if generator over frequency/under frequency fault registered | On Contact 5 | Disabled Contact on pin 1-12 | Settable via Keypad on Controller or Windows Software
165 | Ann. RWL Fault | Selected contact is activated if RWL fault registered. | On Contact 8 | Disabled Contact on pin 1-12 | Settable via Keypad on Controller or Windows Software
166 | Ann. Charging alternator/ V-belt | Selected contact is activated if Charging alternator/V-belt fault registered. | On Contact 6 | Disabled Contact on pin 1-12 | Settable via Keypad on Controller or Windows Software
167 | Ann. Fail to Start | Selected contact is activated if Fail to Start fault registered. | On Contact 11 | Disabled Contact on pin 1-12 | Settable via Keypad on Controller or Windows Software
168 | Ann. Fail to stop | Selected contact is activated if Fail to stop fault registered. | On Contact 12 | Disabled Contact on pin 1-12 | Settable via Keypad on Controller or Windows Software
169 | Ann. Current Unbalance | Selected contact is activated if Current Unbalance fault registered. | No Annunciation | Disabled Contact on pin 1-12 | Settable via Keypad on Controller or Windows Software
170 | Ann. Fuel Open | Selected contact is activated if fuel sensor is open. | No Annunciation | Disabled Contact on pin 1-12 | Settable via Keypad on Controller or Windows Software
171 | Ann. LLOP Open | Selected contact is activated if LLOP sensor is open. | No Annunciation | Disabled Contact on pin 1-12 | Settable via Keypad on Controller or Windows Software
172 | Ann. HET Open | Selected contact is activated if HET sensor is open. | No Annunciation | Disabled Contact on pin 1-12 | Settable via Keypad on Controller or Windows Software
173 | Ann. Canopy Temperature | Selected contact is activated if Canopy Temperature is high. | No Annunciation | Disabled Contact on pin 1-12 | Settable via Keypad on Controller or Windows Software
174 | Ann. Fire | Selected contact is activated if ﬁre fault registered. | No Annunciation | Disabled Contact on pin 1-12 | Settable via Keypad on Controller or Windows Software
175 | Ann. Oil Temperature | Selected contact is activated if Oil Temperature is high | No Annunciation | Disabled Contact on pin 1-12 | Settable via Keypad on Controller or Windows Software
176 | Ann. Oil level | Selected contact is activated if Oil level is low. | No Annunciation | Disabled Contact on pin 1-12 | Settable via Keypad on Controller or Windows Software
177 | Ann. Service Due | Selected contact is activated if Service is due. | No Annunciation | Disabled Contact on pin 1-12 | Settable via Keypad on Controller or Windows Software
178 | Ann. Battery NOK | Selected contact is activated if battery voltage is unhealthy | No Annunciation | Disabled Contact on pin 1-12 | Settable via Keypad on Controller or Windows Software
179 | Ann. common Fault | Selected contact is activated if generator stopped on any fault | On Contact 4 | Disabled Contact on pin 1-12 | Settable via Keypad on Controller or Windows Software
180 | Ann. Half Fuel Warning | Selected contact is activated if low fuel warning is generated | On Contact 9 | Disabled Contact on pin 1-12 | Settable via Keypad on Controller or Windows Software
181 | Ann. C Door Open | Selected contact is activated if Canopy Door is opened | No Annunciation | Disabled Contact on pin 1-12 | Settable via Keypad on Controller or Windows Software
182 | Ann. Gen. Rev. power | Selected contact is activated if Res. Power High | No Annunciation | Disabled Contact on pin 1-12 | Settable via Keypad on Controller or Windows Software
183 | Ann. EGR Warn | Selected contact is activated if any EGR Warning is active | No Annunciation | Disabled Contact on pin 1-12 | Settable via Keypad on Controller or Windows Software
184 | Ann. NCD Warn | Selected contact is activated if NCD Warning is active | No Annunciation | Disabled Contact on pin 1-12 | Settable via Keypad on Controller or Windows Software
185 | Ann. NCD Fault | Selected contact is activated if NCD Fault is active | No Annunciation | Disabled Contact on pin 1-12 | Settable via Keypad on Controller or Windows Software
186 | Ann. CPCB4+ Audio | Selected contact is activated according to CPCB4+ Audio indication requirements (Active every 5 seconds for 2 seconds when NCD Warning active and Active every 2 seconds for 2 seconds when NCD Fault is acive other wise not active) | No Annunciation | Disabled Contact on pin 1-12 | Settable via Keypad on Controller or Windows Software
187 | Device Id | Mod bus device ID | 1 | 1-247 | Settable via Keypad on Controller or Windows Software
188 | Baud Rate | RS 485 Communication Baud rate | 9600 | 1200 2400 4800 9600 19200 | Settable via Keypad on Controller or Windows Software
189 | Parity | RS 485 Communication Parity Bits | None | Even Odd None | Settable via Keypad on Controller or Windows Software
190 | Stop Bit | RS 485 Communication Stop Bits | 1 | 1 2 | Settable via Keypad on Controller or Windows Software

## Setting-TMTL-15KVA (hidden)
Controller: | ECON-MAN-IND
Firmware | v2.04/v2.06
No. | Name Of Setting On LCD Display | Setting Description | Default setting | Setting Range | Default setting for 15KVA TMTL Genset | Edit Options | Remarks
1 | Suppliers | Company logo and default parameter is set as per system suppliers. | Procom | PROCOM TMTL M&M | TMTL | Only Settable via Windows Software
2 | System Conﬁg | ECON provides complete ﬂexibility in system designing; it is possible to select manual operation for DG phases. | Generator 3 Phase | Generator 1 Phase Generator 3 Phase | Generator 1 Phase | Settable via Keypad on Controller or Windows Software
3 | Solenoid Type | Pull To Start In this mode fuel solenoid contact changes from Open to Close at the time of cranking and remains close till the gen set is running. For stopping the generator this contact opens. Pull To Stop In this mode fuel solenoid contact remains open at the time of cranking and till the gen set is running. For stopping the generator this contact closes for a user programmed time. | Pull To Stop | Pull to Stop Pull to Start | Pull To Stop | Only Settable via Windows Software
4 | LLOP Sensor Type | Select the installed sensor for LLOP | TMTL | User Deﬁned Type A M&M MNEPL VE TMTL HUAFANG TATA GC(VDO) GC(MURPHY) 4-20MA M&M-2 Disabled * | TMTL | Only Settable via Windows Software
5 | LLOP Sensor R1 | R1 to R10 = Resistance Value V1 to V10 = Corresponding pressure value. These table are used when sensor type is selected as user deﬁned. | 10Ω | 0-999Ω | 10Ω | Only Settable via Windows Software
6 | LLOP Sensor V1 |  | 0 Bar | 0.0-10.0 Bar | 0 Bar | Only Settable via Windows Software
7 | LLOP Sensor R2 |  | 29Ω | 0-999Ω | 29Ω | Only Settable via Windows Software
8 | LLOP Sensor V2 |  | 1 Bar | 0.0-10.0 Bar | 1 Bar | Only Settable via Windows Software
9 | LLOP Sensor R3 |  | 38Ω | 0-999Ω | 38Ω | Only Settable via Windows Software
10 | LLOP Sensor V3 |  | 1.5Bar | 0.0-10.0 Bar | 1.5Bar | Only Settable via Windows Software
11 | LLOP Sensor R4 |  | 48Ω | 0-999Ω | 48Ω | Only Settable via Windows Software
12 | LLOP Sensor V4 |  | 2Bar | 0.0-10.0 Bar | 2Bar | Only Settable via Windows Software
13 | LLOP Sensor R5 |  | 57Ω | 0-999Ω | 57Ω | Only Settable via Windows Software
14 | LLOP Sensor V5 |  | 2.5Bar | 0.0-10.0 Bar | 2.5Bar | Only Settable via Windows Software
15 | LLOP Sensor R6 |  | 67Ω | 0-999Ω | 67Ω | Only Settable via Windows Software
16 | LLOP Sensor V6 |  | 3Bar | 0.0-10.0 Bar | 3Bar | Only Settable via Windows Software
17 | LLOP Sensor R7 |  | 86Ω | 0-999Ω | 86Ω | Only Settable via Windows Software
18 | LLOP Sensor V7 |  | 4Bar | 0.0-10.0 Bar | 4Bar | Only Settable via Windows Software
19 | LLOP Sensor R8 |  | 105Ω | 0-999Ω | 105Ω | Only Settable via Windows Software
20 | LLOP Sensor V8 |  | 5Bar | 0.0-10.0 Bar | 5Bar | Only Settable via Windows Software
21 | LLOP Sensor R9 |  | 124Ω | 0-999Ω | 124Ω | Only Settable via Windows Software
22 | LLOP Sensor V9 |  | 6Bar | 0.0-10.0 Bar | 6Bar | Only Settable via Windows Software
23 | LLOP Sensor R10 |  | 143Ω | 0-999Ω | 143Ω | Only Settable via Windows Software
24 | LLOP Sensor V10 |  | 7Bar | 0.0-10.0 Bar | 7Bar | Only Settable via Windows Software
25 | Fuel Sensor | Select the installed sensor for Fuel The installed sensor should be Electronics or Linear if system suppliers as TMTL | .5-4.5(0-100%) | User Deﬁned Type A Sam-0 Sam-1 Electronics Linear 0-5V(0-100%) Disabled* | Electronics | Only Settable via Windows Software
26 | Fuel Sensor R1 | R1 to R10 = Resistance Value V1 to V10 = Corresponding fuel level in %. These table are used when sensor type is selected as user deﬁned. | 10Ω | 0-999Ω | 10Ω | Only Settable via Windows Software
27 | Fuel Sensor V1 |  | 0 | 0-100% | 0 | Only Settable via Windows Software
28 | Fuel Sensor R2 |  | 29Ω | 0-999Ω | 29Ω | Only Settable via Windows Software
29 | Fuel Sensor V2 |  | 0.1 | 0-100% | 10% | Only Settable via Windows Software
30 | Fuel Sensor R3 |  | 48Ω | 0-999Ω | 48Ω | Only Settable via Windows Software
31 | Fuel Sensor V3 |  | 0.2 | 0-100% | 20% | Only Settable via Windows Software
32 | Fuel Sensor R4 |  | 67Ω | 0-999Ω | 67Ω | Only Settable via Windows Software
33 | Fuel Sensor V4 |  | 0.3 | 0-100% | 30% | Only Settable via Windows Software
34 | Fuel Sensor R5 |  | 86Ω | 0-999Ω | 86Ω | Only Settable via Windows Software
35 | Fuel Sensor V5 |  | 0.4 | 0-100% | 40% | Only Settable via Windows Software
36 | Fuel Sensor R6 |  | 105Ω | 0-999Ω | 105Ω | Only Settable via Windows Software
37 | Fuel Sensor V6 |  | 0.5 | 0-100% | 50% | Only Settable via Windows Software
38 | Fuel Sensor R7 |  | 124Ω | 0-999Ω | 124Ω | Only Settable via Windows Software
39 | Fuel Sensor V7 |  | 0.6 | 0-100% | 60% | Only Settable via Windows Software
40 | Fuel Sensor R8 |  | 143Ω | 0-999Ω | 143Ω | Only Settable via Windows Software
41 | Fuel Sensor V8 |  | 0.7 | 0-100% | 70% | Only Settable via Windows Software
42 | Fuel Sensor R9 |  | 181Ω | 0-999Ω | 181Ω | Only Settable via Windows Software
43 | Fuel Sensor V9 |  | 0.9 | 0-100% | 90% | Only Settable via Windows Software
44 | Fuel Sensor R10 |  | 200Ω | 0-999Ω | 200Ω | Only Settable via Windows Software
45 | Fuel Sensor V10 |  | 100 | 0-100% | 100 | Only Settable via Windows Software
46 | Fuel Tank Capacity | The capacity of the fuel tank in litres. | 250 Ltr | Disabled 0-999Ltr | 250 Ltr | Only Settable via Windows Software
47 | HET Sensor | Select the installed sensor for HET The installed sensor should be either TMTL AIR 1C or TMTL AIR 3C or TMTL WATER if system suppliers as TMTL | TMTL Range 2 | User Deﬁned Type A M&M MNEPL VE TMTL RANGE 1 TMTL RANGE 2 TMTL WATER HUAFANG TATA GC(VDO) GC(MURPHY) Disabled * | TMTL RANGE 2 | Only Settable via Windows Software
48 | HET Sensor R1 | R1 to R10 = Resistance Value V1 to V10 = Corresponding temperature in °C. These table are used when sensor type is selected as user deﬁned. | 540Ω | 0-9999Ω | 540Ω | Only Settable via Windows Software
49 | HET Sensor V1 |  | 40℃ | 0-300 Celsius | 40℃ | Only Settable via Windows Software
50 | HET Sensor R2 |  | 458Ω | 0-9999Ω | 458Ω | Only Settable via Windows Software
51 | HET Sensor V2 |  | 45℃ | 0-300 Celsius | 45℃ | Only Settable via Windows Software
52 | HET Sensor R3 |  | 222Ω | 0-9999Ω | 222Ω | Only Settable via Windows Software
53 | HET Sensor V3 |  | 65℃ | 0-300 Celsius | 65℃ | Only Settable via Windows Software
54 | HET Sensor R4 |  | 120Ω | 0-9999Ω | 120Ω | Only Settable via Windows Software
55 | HET Sensor V4 |  | 85℃ | 0-300 Celsius | 85℃ | Only Settable via Windows Software
56 | HET Sensor R5 |  | 93Ω | 0-9999Ω | 93Ω | Only Settable via Windows Software
57 | HET Sensor V5 |  | 90℃ | 0-300 Celsius | 90℃ | Only Settable via Windows Software
58 | HET Sensor R6 |  | 80Ω | 0-9999Ω | 80Ω | Only Settable via Windows Software
59 | HET Sensor V6 |  | 95℃ | 0-300 Celsius | 95℃ | Only Settable via Windows Software
60 | HET Sensor R7 |  | 70Ω | 0-9999Ω | 70Ω | Only Settable via Windows Software
61 | HET Sensor V7 |  | 100℃ | 0-300 Celsius | 100℃ | Only Settable via Windows Software
62 | HET Sensor R8 |  | 60Ω | 0-9999Ω | 60Ω | Only Settable via Windows Software
63 | HET Sensor V8 |  | 105℃ | 0-300 Celsius | 105℃ | Only Settable via Windows Software
64 | HET Sensor R9 |  | 53Ω | 0-9999Ω | 53Ω | Only Settable via Windows Software
65 | HET Sensor V9 |  | 110℃ | 0-300 Celsius | 110℃ | Only Settable via Windows Software
66 | HET Sensor R10 |  | 46Ω | 0-9999Ω | 46Ω | Only Settable via Windows Software
67 | HET Sensor V10 |  | 115℃ | 0-300 Celsius | 115℃ | Only Settable via Windows Software
68 | Sensor Open | User can select the action to be taken in case of sensor open, it can be configured as a fault, or as warning | Disabled | Disabled * Warning | Disabled | Settable via Keypad on Controller or Windows Software
69 | CT Ratio | Current Transformer ratio | 1 | 1-100 | 15 | Only Settable via Windows Software
70 | Gen. RPM | Engine RPM Type | 1500 RPM | 1500RPM 3000RPM | 1500 RPM | Only Settable via Windows Software
71 | Contact ON Pin 32 | These are three programmable output which can be configured for any one function from the list | Heater/choke | None Unit Healthy Load Warning Fuel Pump Heater /Choke Pull Solenoid | Heater/choke | Only Settable via Windows Software
72 | Contact ON Pin 31 | These are three programmable output which can be conﬁgured for any one function from the list | None | None Unit Healthy Load Warning Fuel Pump Heater /Choke Pull Solenoid | None | Settable via Keypad on Controller or Windows Software
73 | Contact ON Pin 30 | These are three programmable output which can be conﬁgured for any one function from the list | None | None Unit Healthy Load Warning Fuel Pump Heater / Choke Pull Solenoid | None | Settable via Keypad on Controller or Windows Software
74 | Over Load KW | The Power(KW) above which the over load fault monitoring will start. The timer for it is over load delay. This fault is only enabled while the generator is running. On expiry of the timer the generator is stopped | 9.2 KW | 1.0-20.0 KW | 13.2 KW | Only Settable via Windows Software
75 | Over Current | The current above which the over current fault monitoring will start. The timer for it is over load delay. This fault is only enabled while the generator is running. On expiry of thetimer the generator is stopped | 50.1 A | 1.0-150 A | 71.8 A | Only Settable via Windows Software
76 | Over Load Delay | This is the timer for the over load condition either due to over KW or over current. On expiry of this timer the engine shall be stopped | 10 Sec | 1-15 Sec | 10 Sec | Only Settable via Windows Software
77 | High Load KW | The Power(KW) above which the High load fault monitoring will start. The timer for it is High load delay. This fault is only enabled while the generator is running. On expiry of the timer the generator is stopped | Disabled | Disabled* 1.0-150KW | 12.0 KW | Only Settable via Windows Software
78 | High Load Delay | This is the timer for the High load Condition. On expiry of this timer the engine shall be stopped | 10 Sec | 1-9999Sec | 3600 Sec | Only Settable via Windows Software
79 | Reverse power | The Power(KW) above which the Res. Power fault monitoring will start. The timer for it is Res. Power delay. This fault is only enabled while the generator is running. On expiry of the timer the generator is stopped | Disabled | Disable* 0.5-150 KW | 0.5 | Settable via Keypad on Controller or Windows Software
80 | Reverse power delay | This is the timer for the Res. Power Condition. On expiry of this timer the engine shall be stopped | 10 Sec | 1-999 Sec | 1 Sec | Settable via Keypad on Controller or Windows Software
81 | Digital Input 1 | This can be conﬁgured for one out the listed below Parameters. RWL Oil Level Oil Temperature Canopy Temperature | RWL | RWL Oil Level Oil Temp. Canopy Temp. | RWL | Settable via Keypad on Controller or Windows Software
82 | Digital Input 1 Polarity | The polarity of digital input can be changed either normally open or normally close. | Normally open | Normally Open Normally Close | Normally open | Settable via Keypad on Controller or Windows Software
83 | Digital Input 2 | This can be configured for one out the listed below Parameters. LLOP Oil Level Oil Temperature Canopy Temperature | LLOP | LLOP Oil Level Oil Temp. Canopy Temp. | LLOP | Settable via Keypad on Controller or Windows Software
84 | Digital Input 2 Polarity | The polarity of digital input can be changed either normally open or normally close. | Normally open | Normally Open Normally Close | Normally open | Settable via Keypad on Controller or Windows Software
85 | Digital Input 3 | This can be configured for one out the listed below Parameters. Low Fuel Oil Level, Oil Temperature Canopy Temperature | Low Fuel | Low Fuel Oil Level Oil Temp. Canopy Temp. | Low Fuel | Only Settable via Windows Software
86 | Digital Input 3 Polarity | The polarity of digital input can be changed either normally open or normally close. | Normally open | Normally Open Normally Close | Normally open | Only Settable via Windows Software
87 | Digital Input 4 | This can be configured for one out the listed below Parameters. HET Oil Level Oil Temperature Canopy Temperature | HET/HWT | HET/HWT Oil Level Oil Temp. Canopy Temp. | HET/HWT | Settable via Keypad on Controller or Windows Software
88 | Digital Input 4 Polarity | The polarity of digital input can be changed either normally open or normally close. | Normally open | Normally Open Normally Close | Normally open | Settable via Keypad on Controller or Windows Software
89 | Digital Input 5 | This can be configured for one of the listed below Parameters. Canopy door open Oil Level Oil Temperature Canopy Temperature V- belt Ext-1 Ext-2 EGR Warning EGR Fault Padmini EGR | C Door open | C Door open V-belt Ext-1, Ext-2 EGR Warning EGR Fault Padmini EGR | EGR Fault | Settable via Keypad on Controller or Windows Software
90 | Digital Input 5 Polarity | The polarity of digital input can be changed either normally open or normally close. | Normally open | Normally Open Normally Close | Normally Close | Settable via Keypad on Controller or Windows Software
91 | Digital Input 6 | This can be configured for one of the listed below Parameters. Fire Oil Level Oil Temperature Canopy Temperature V- belt Ext-1 Ext-2 EGR Warning EGR Fault Padmini EGR | Fire | Fire Oil Level Oil Temp. Canopy Temp. V-belt Ext-1, Ext-2 EGR Warning EGR Fault Padmini EGR | EGR Warning | Settable via Keypad on Controller or Windows Software
92 | Digital Input 6 Polarity | The polarity of digital input can be changed either normally open or normally close. | Normally open | Normally Open Normally Close | Normally open | Settable via Keypad on Controller or Windows Software
93 | Digital Input 7 | This can be configured for one of the listed below Parameters. Half Fuel Warning Oil Level Oil Temperature Canopy Temperature V- belt Ext-1 Ext-2 EGR Warning EGR Fault Padmini EGR | Half Fuel Warning | Half Fuel Warning Oil Level Oil Temp. Canopy Temp. V-belt Ext-1, Ext-2 EGR Warning EGR Fault Padmini EGR | Half Fuel Warning | Only Settable via Windows Software
94 | Digital Input 7 Polarity | The polarity of digital input can be changed either normally open or normally close. | Normally open | Normally Open Normally Close | Normally open | Only Settable via Windows Software
95 | Digital Input 8 | This can be conﬁgured for one of the listed below Parameters. Oil Level Oil Temperature Canopy Temperature V-belt Ext-1 Ext-2 EGR Warning EGR Fault Padmini EGR | Canopy Temp. | Oil Level Oil Temp. Canopy Temp. V-belt Ext-1, Ext-2 EGR Warning EGR Fault Padmini EGR | Canopy Temp. | Settable via Keypad on Controller or Windows Software
96 | Digital Input 8 Polarity | The polarity of digital input can be changed either normally open or normally close. | Normally open | Normally Open Normally Close | Normally open | Settable via Keypad on Controller or Windows Software
97 | Fan high current | Maximum limit for fan | 1.1A | Disable* 0-3.5A | 2.5A | Only Settable via Windows Software
98 | Fan low current | Minimum Limit For fan current. This Parameter is disabled if the above paramters is disabled. | 0.2A | 0-3.5A | 0.2A | Only Settable via Windows Software
99 | Fan current delay | This is the timer for fan current trip. | 25 Sec | 1-60 Sec | 25 Sec | Only Settable via Windows Software | Default 15 sec in v2.04 and 25 sec in v2.06
100 | Generator O/V | Max. Permissible Generator voltage, above this the Generator voltage is treated unhealthy & the Generator is stopped on voltage fault. | 285V | 150-300V | 265 V | Only Settable via Windows Software
101 | Generator U/V | Min. permissible Generator voltage, below this the Generator voltage is treated unhealthy & the Generator is stopped on voltage fault. | 185V | 100-300V | 190 V | Only Settable via Windows Software | Range was 100-200V in v2.04 and 100-300V in v2.06
102 | Gen Voltage Delay | Duration for which generator Over/Under voltage condition can be tolerated before stopping the Generator. | 10 Sec | 1-300 Sec | 10 Sec | Only Settable via Windows Software
103 | Generator Over Frq. | Max. Permissible Generator Frq., above this the Generator Frq. is treated unhealthy & the Generator is stopped on Frq. fault. | 55 Hz | 25-70Hz Disable* | 55 Hz | Only Settable via Windows Software
104 | Generator Under Frq. | Min. permissible Generator Frq., below this the Generator Frq. is treated unhealthy & the Generator isstopped Frq. fault. | 45 Hz | Disable* 25-70Hz | 45 Hz | Only Settable via Windows Software
105 | Gen Frq. Delay | Duration for which Generator Over /Under Frq. condition can be tolerated before stopping the Generator. This setting is not available if (4)&(5) are disabled | 5 sec | 1-300 Sec. | 5 Sec | Only Settable via Windows Software
106 | Current Unbalance | The maximum permissible current unbalance in %. The unbalance starts only after the system is loaded to 25%of its capacity | Disabled | 5-100% Disable | Disabled | Only Settable via Windows Software
107 | Current Unbalance Delay | Duration for which the current unbalance can be tolerated before triggering the fault | 10 Sec | 1-999Sec | 10 Sec | Only Settable via Windows Software
108 | Pickup Voltage | This parameter speciﬁes the generator voltage at which it is presumed to have started and crank has to be terminated | 30V | 30-150V | 30V | Only Settable via Windows Software
109 | Pick Up RPM | This parameter speciﬁes the edge RPM ( deﬁne for DG voltage) at which crank shall be terminated. | 300RPM | 300-1200 | 300RPM | Only Settable via Windows Software
110 | First Service Due Hr | Time, in hours, for next service due warning. | 500 | 1-999 Hrs | 50Hrs | Settable via Keypad on Controller or Windows Software
111 | Later service due hr | Time, in hours, for next service due warning. | 500 | 1-999 Hrs | 500Hrs | Settable via Keypad on Controller or Windows Software
112 | Crank Cut Method | Auto disconnects the crank command on detection of either voltage build-up/ voltage or oil pressure build up | Volt+Hz+Switch | Volt+Hz Volt+Hz+Switch Volt+Hz+Sensor Volt+Hz+Sensor+Switch | Volt+Hz+Switch | Only Settable via Windows Software
113 | Pick Up KVA | If the current level crosses this limit the contact is energized after the programmed supervision time | 8 KVA | 1-9999 KVA | 8 KVA | Only Settable via Windows Software
114 | Reset KVA | If the current level falls below this limit the contact is de-energized after the programmed supervision time. | 8 KVA | 1-9999 KVA | 8 KVA | Only Settable via Windows Software
115 | KVA Warning Delay | The supervision time for the above 2 parameters. | 5 Sec | 1-999 Sec | 5 Sec | Only Settable via Windows Software
116 | Choke Pre time | Keep the choke for this time before the engine has started. | Disabled | Disable* 1-999 Sec | Disabled | Settable via Keypad on Controller or Windows Software
117 | Choke Post time | Keep the choke for this time after the engine has started. | Disabled | Disable* 1-999 Sec | Disabled | Settable via Keypad on Controller or Windows Software
118 | Pump Pre Time | Activate the Pump by this time before cranking | 2 Sec | 1-999Sec | 2 Sec | Only Settable via Windows Software
119 | Generator Warmup Delay | The load is switched to Generator after expiry of this time | 0 Sec | 0-999Sec | 15 Sec | Settable via Keypad on Controller or Windows Software
120 | Generator Recooling Delay | The time for which the Generator is allowed to run on no load before switching off | 30 Sec | 0-999Sec | 30 Sec | Settable via Keypad on Controller or Windows Software
121 | Fuel Warn Level | Monitoring value of fuel level below which fuel level warning is generated. | 50% | Disable* 10-80 % | 50% | Only Settable via Windows Software
122 | Fuel Warn Delay | Monitoring time of fuel level after which fuel level warning is generated. | 10 Sec | 1-99 Sec | 10 Sec | Only Settable via Windows Software
123 | Fuel Trip Level | Monitoring value of fuel level below which fuel level trip is generated. | 15% | 10-81 % Disable | 15% | Only Settable via Windows Software
124 | Fuel Trip Delay | Monitoring time of fuel level after which fuel level trip is generated. | 10 Sec | 1-999 Sec | 10 Sec | Only Settable via Windows Software
125 | LLOP Trip Level | Monitoring value of lube oil pressure below which LLOP trip is generated. | 0.7 Kg/Cm2 | 0.3-8.5 Kg/cm2 Disable | 0.7 Kg/Cm2 | Only Settable via Windows Software
126 | LLOP Trip Delay | Monitoring time of lube oil pressure after which LLOP trip is generated. | 10 Sec | 0-999 Sec | 10 Sec | Only Settable via Windows Software
127 | HET Trip Level | Monitoring value of water temperature above which HET trip is generated. | Disabled | 40-251 Disabled* | Disabled | Only Settable via Windows Software
128 | HET Trip Delay | Monitoring time of water temperature after which HET trip is generated. | 10 Sec | 10-60 Sec | 10 Sec | Only Settable via Windows Software
129 | Digital Input 1 Delay | Delay for programmable digital input. Digital input are explained above. | 10 Sec | 1-99 Sec | 10 Sec | Settable via Keypad on Controller or Windows Software
130 | Digital Input 2 Delay | Delay for programmable digital input. Digital input are explained above. | 10 Sec | 1-99 Sec | 10 Sec | Settable via Keypad on Controller or Windows Software
131 | Digital Input 3 Delay | Delay for programmable digital input. Digital input are explained above. | 10 Sec | 1-99 Sec | 10 Sec | Only Settable via Windows Software
132 | Digital Input 4 Delay | Delay for programmable digital input. Digital input are explained above. | 10 Sec | 1-99 Sec | 10 Sec | Settable via Keypad on Controller or Windows Software
133 | Digital Input 5 Delay | Delay for programmable digital input. Digital input are explained above. | 10 Sec | 1-99 Sec | 10 Sec | Settable via Keypad on Controller or Windows Software
134 | Digital Input 6 Delay | Delay for programmable digital input. Digital input are explained above. | 10 Sec | 1-299 Sec | 10 Sec | Settable via Keypad on Controller or Windows Software
135 | Digital Input 7 Delay | Delay for programmable digital input. Digital input are explained above. | 10 Sec | 1-99 Sec | 10 Sec | Only Settable via Windows Software
136 | Digital Input 8 Delay | Delay for programmable digital input. Digital input are explained above. | 10 Sec | 1-99 Sec | 10 Sec | Settable via Keypad on Controller or Windows Software
137 | Chg Alt-V Belt Delay | Duration for which the V-Belt signal should be continuously deactive to be recognized as a fault and action initiated. This fault is only enabled while the generator is running. | 180 Sec | Disable* 1-299 Sec | Disabled | Settable via Keypad on Controller or Windows Software | Default value was 180 second in v2.04 and Disabled in v2.06
138 | Hooter ON Time | Duration for which the hooter shall be ON, if not externally reset, while announcing a fault. | 30 Sec | 1-299 Sec | 30 Sec | Settable via Keypad on Controller or Windows Software
139 | Crank ON Time | Maximum crank time | 2.0 Sec | 0.5-20 Sec | 2.0 Sec | Settable via Keypad on Controller or Windows Software | Range was 0.5-5 Seconds in v2.04 and 0.5-20 seconds in v2.06
140 | Crank Gap Time | The delay between two successive cranks | 10 Sec | 1-99 Sec | 10 Sec | Settable via Keypad on Controller or Windows Software
141 | Crank Attempts | The maximum number of cranks that shall be issued to start the Engine | 3 | 3-5 | 3 | Settable via Keypad on Controller or Windows Software
142 | Solenoid ON time | The time for which stop solenoid will be kept active while stopping the engine | 35 Sec | 1-99 Sec | 35 Sec | Settable via Keypad on Controller or Windows Software
143 | Disp Auto Scroll | Setting ON will enable Auto Scroll of display. OFF: No scroll and next parameter can be viewed by pressing next switch | ON | ON/OFF | ON | Settable via Keypad on Controller or Windows Software
144 | Scrolling Delay | After this duration next parameter Displayed on Display. | 10 Sec | 5-99Sec | 10 Sec | Settable via Keypad on Controller or Windows Software
145 | Battery UV Warning | Min. permissible battery voltage, below this the voltage is treated unhealthy & warning is generated. | 10.0 V | Disabled* 7.9-12V | 10.0 V | Settable via Keypad on Controller or Windows Software
146 | Battery OV Warning | Max. permissible battery voltage, above this the voltage is treated unhealthy & warning is generated. | 14.5 V | 12-30V Disabled* | 16.5 V | Settable via Keypad on Controller or Windows Software
147 | Canopy Over Temp. | Monitoring value of Canopy Temp. Above which Canopy temp. Is generated. | 27.0 Celsius | 15.0-99.9 Celsius | 60 deg Celsius | Settable via Keypad on Controller or Windows Software
148 | Canopy Over Temp. Delay | Monitoring Time value of Canopy Temp. After which Canopy temp. Is generated. | 20 sec | 1-999Sec | 20 sec | Settable via Keypad on Controller or Windows Software
149 | NCD Strategy | Enable or Disable NCD (NOx Control Diagnostic) System as per CPCB4+ guidelines | Disabled* | Disabled* Enabled | Disabled* | Settable via Keypad on Controller or Windows Software
150 | NCD Warn Hrs | Set the time in Hrs while Generator is running after which NCD Warning will get activated if any EGR warning remains in the system during this whole period. | 36.00 Hrs | 0.01-99.99 Hrs | 36.00 Hrs | Settable via Keypad on Controller or Windows Software
151 | NCD Fault Hrs | Set the time in Hrs while Generator is running after which NCD Fault will get activated if any EGR warning remains in the system during this whole period. | 72.00 Hrs | 0.01-99.99 Hrs | 72.00 Hrs | Settable via Keypad on Controller or Windows Software
152 | NCD Heal Hrs | Set the time in Hrs while Generator is running after which NCD Error timer will get reset if no EGR warning remains in the system during this whole period. | 40.00 Hrs | 0.01-99.99 Hrs | 40.00 Hrs | Settable via Keypad on Controller or Windows Software
153 | Ann. DG On | Selected contact is activated if Generator is on | No Annuciation | No Annunciation Contact on pin 1-12 | On Contact 1 | Settable via Keypad on Controller or Windows Software
154 | Ann. DG Off | Selected contact is activated if Generator is off. | No Annuciation | No Annunciation Contact on pin 1-12 | No Annuciation | Settable via Keypad on Controller or Windows Software
155 | Ann. DG On Load | Selected contact is activated if Generator is On load | On Contact 7 | No Annunciation Contact on pin 1-12 | On Contact 2 | Settable via Keypad on Controller or Windows Software
156 | Ann. Unit OK | Selected contact is activated if unit is ok. | No Annuciation | No Annunciation Contact on pin 1-12 | No Annuciation | Settable via Keypad on Controller or Windows Software
157 | Ann. Fuel Trip | Selected contact is activated if fuel fault registered | On Contact 10 | No Annunciation Contact on pin 1-12 | No Annuciation | Settable via Keypad on Controller or Windows Software
158 | Ann. LLOP Trip | Selected contact is activated if LLOP fault registered | On Contact 1 | No Annunciation Contact on pin 1-12 | On Contact 5 | Settable via Keypad on Controller or Windows Software
159 | Ann. HET Trip | Selected contact is activated if HET fault registered. | On Contact 2 | No Annunciation Contact on pin 1-12 | On Contact 8 | Settable via Keypad on Controller or Windows Software
160 | Ann. DG Voltage | Selected contact is activated if Generator voltage is healthy. | No Annuciation | No Annunciation Contact on pin 1-12 | No Annuciation | Settable via Keypad on Controller or Windows Software
161 | Ann. Emergency | Selected contact is activated if emergency fault is registered. | No Annuciation | No Annunciation Contact on pin 1-12 | No Annuciation | Settable via Keypad on Controller or Windows Software
162 | Ann. DG Overload | Selected contact is activated if generator is overloaded. | On Contact 3 | No Annunciation Contact on pin 1-12 | On Contact 3 | Settable via Keypad on Controller or Windows Software
163 | Ann. DG High Load | Selected contact is activated if generator is highloaded. | No Annuciation | No Annunciation Contact on pin 1-12 | No Annuciation | Settable via Keypad on Controller or Windows Software
164 | Ann. DG Frequency | Selected contact is activated if generator over frequency/under frequency fault registered | On Contact 5 | No Annunciation Contact on pin 1-12 | No Annunciation | Settable via Keypad on Controller or Windows Software
165 | Ann. RWL Fault | Selected contact is activated if RWL fault registered. | On Contact 8 | No Annunciation Contact on pin 1-12 | No Annunciation | Settable via Keypad on Controller or Windows Software
166 | Ann. Charging alternator/ V-belt | Selected contact is activated if Charging alternator/V-belt fault registered. | On Contact 6 | No Annunciation Contact on pin 1-12 | No Annunciation | Settable via Keypad on Controller or Windows Software
167 | Ann. Fail to Start | Selected contact is activated if Fail to Start fault registered. | On Contact 11 | No Annunciation Contact on pin 1-12 | On Contact 11 | Settable via Keypad on Controller or Windows Software
168 | Ann. Fail to stop | Selected contact is activated if Fail to stop fault registered. | On Contact 12 | No Annunciation Contact on pin 1-12 | On Contact 12 | Settable via Keypad on Controller or Windows Software
169 | Ann. Current Unbalance | Selected contact is activated if Current Unbalance fault registered. | No Annunciation | No Annunciation Contact on pin 1-12 | No Annunciation | Settable via Keypad on Controller or Windows Software
170 | Ann. Fuel Open | Selected contact is activated if fuel sensor is open. | No Annunciation | No Annunciation Contact on pin 1-12 | No Annunciation | Settable via Keypad on Controller or Windows Software
171 | Ann. LLOP Open | Selected contact is activated if LLOP sensor is open. | No Annunciation | No Annunciation Contact on pin 1-12 | No Annunciation | Settable via Keypad on Controller or Windows Software
172 | Ann. HET Open | Selected contact is activated if HET sensor is open. | No Annunciation | No Annunciation Contact on pin 1-12 | No Annunciation | Settable via Keypad on Controller or Windows Software
173 | Ann. Canopy Temperature | Selected contact is activated if Canopy Temperature is high. | No Annunciation | No Annunciation Contact on pin 1-12 | No Annunciation | Settable via Keypad on Controller or Windows Software
174 | Ann. Fire | Selected contact is activated if ﬁre fault registered. | No Annunciation | No Annunciation Contact on pin 1-12 | No Annunciation | Settable via Keypad on Controller or Windows Software
175 | Ann. Oil Temperature | Selected contact is activated if Oil Temperature is high | No Annunciation | No Annunciation Contact on pin 1-12 | No Annunciation | Settable via Keypad on Controller or Windows Software
176 | Ann. Oil level | Selected contact is activated if Oil level is low. | No Annunciation | No Annunciation Contact on pin 1-12 | No Annunciation | Settable via Keypad on Controller or Windows Software
177 | Ann. Service Due | Selected contact is activated if Service is due. | No Annunciation | No Annunciation Contact on pin 1-12 | No Annunciation | Settable via Keypad on Controller or Windows Software
178 | Ann. Battery NOK | Selected contact is activated if battery voltage is unhealthy | No Annunciation | No Annunciation Contact on pin 1-12 | No Annunciation | Settable via Keypad on Controller or Windows Software
179 | Ann. common Fault | Selected contact is activated if generator stopped on any fault | On Contact 4 | No Annunciation Contact on pin 1-12 | On Contact 4 | Settable via Keypad on Controller or Windows Software
180 | Ann. Half Fuel Warning | Selected contact is activated if low fuel warning is generated | On Contact 9 | No Annunciation Contact on pin 1-12 | On Contact 9 | Settable via Keypad on Controller or Windows Software
181 | Ann. C Door Open | Selected contact is activated if Canopy Door is opened | No Annunciation | No Annunciation Contact on pin 1-12 | No Annunciation | Settable via Keypad on Controller or Windows Software
182 | Ann. Gen. Rev. power | Selected contact is activated if Res. Power High | No Annunciation | No Annunciation Contact on pin 1-12 | No Annunciation | Settable via Keypad on Controller or Windows Software
183 | Ann. EGR Warn | Selected contact is activated if any EGR Warning is active | No Annunciation | No Annunciation Contact on pin 1-12 | No Annunciation | Settable via Keypad on Controller or Windows Software
184 | Ann. NCD Warn | Selected contact is activated if NCD Warning is active | No Annunciation | No Annunciation Contact on pin 1-12 | No Annunciation | Settable via Keypad on Controller or Windows Software
185 | Ann. NCD Fault | Selected contact is activated if NCD Fault is active | No Annunciation | No Annunciation Contact on pin 1-12 | No Annunciation | Settable via Keypad on Controller or Windows Software
186 | Ann. CPCB4+ Audio | Selected contact is activated according to CPCB4+ Audio indication requirements (Active every 5 seconds for 2 seconds when NCD Warning active and Active every 2 seconds for 2 seconds when NCD Fault is acive other wise not active) | No Annunciation | No Annunciation Contact on pin 1-12 | No Annunciation | Settable via Keypad on Controller or Windows Software
187 | Device Id | Mod bus device ID | 1 | 1-247 | 1 | Settable via Keypad on Controller or Windows Software
188 | Baud Rate | RS 485 Communication Baud rate | 9600 | 1200 2400 4800 9600 19200 | 9600 | Settable via Keypad on Controller or Windows Software
189 | Parity | RS 485 Communication Parity Bits | None | Even Odd None | None | Settable via Keypad on Controller or Windows Software
190 | Stop Bit | RS 485 Communication Stop Bits | 1 | 1 2 | 1 | Settable via Keypad on Controller or Windows Software

## Setting-TMTL-10KVA (hidden)
Controller: | ECON-MAN-IND
Firmware | v2.06
No. | Name Of Setting On LCD Display | Setting Description | Default setting | Setting Range | Default setting for 15KVA TMTL Genset | Edit Options
1 | Suppliers | Company logo and default parameter is set as per system suppliers. | Procom | PROCOM TMTL M&M | TMTL | Only Settable via Windows Software
2 | System Conﬁg | ECON provides complete ﬂexibility in system designing; it is possible to select manual operation for DG phases. | Generator 3 Phase | Generator 1 Phase Generator 3 Phase | Generator 1 Phase | Settable via Keypad on Controller or Windows Software
3 | Solenoid Type | Pull To Start In this mode fuel solenoid contact changes from Open to Close at the time of cranking and remains close till the gen set is running. For stopping the generator this contact opens. Pull To Stop In this mode fuel solenoid contact remains open at the time of cranking and till the gen set is running. For stopping the generator this contact closes for a user programmed time. | Pull To Stop | Pull to Stop Pull to Start | Pull To Stop | Only Settable via Windows Software
4 | LLOP Sensor Type | Select the installed sensor for LLOP | TMTL | User Deﬁned Type A M&M MNEPL VE TMTL HUAFANG TATA GC(VDO) GC(MURPHY) 4-20MA M&M-2 Disabled * | TMTL | Only Settable via Windows Software
5 | LLOP Sensor R1 | R1 to R10 = Resistance Value V1 to V10 = Corresponding pressure value. These table are used when sensor type is selected as user deﬁned. | 10Ω | 0-999Ω | 10Ω | Only Settable via Windows Software
6 | LLOP Sensor V1 |  | 0 Bar | 0.0-10.0 Bar | 0 Bar | Only Settable via Windows Software
7 | LLOP Sensor R2 |  | 29Ω | 0-999Ω | 29Ω | Only Settable via Windows Software
8 | LLOP Sensor V2 |  | 1 Bar | 0.0-10.0 Bar | 1 Bar | Only Settable via Windows Software
9 | LLOP Sensor R3 |  | 38Ω | 0-999Ω | 38Ω | Only Settable via Windows Software
10 | LLOP Sensor V3 |  | 1.5Bar | 0.0-10.0 Bar | 1.5Bar | Only Settable via Windows Software
11 | LLOP Sensor R4 |  | 48Ω | 0-999Ω | 48Ω | Only Settable via Windows Software
12 | LLOP Sensor V4 |  | 2Bar | 0.0-10.0 Bar | 2Bar | Only Settable via Windows Software
13 | LLOP Sensor R5 |  | 57Ω | 0-999Ω | 57Ω | Only Settable via Windows Software
14 | LLOP Sensor V5 |  | 2.5Bar | 0.0-10.0 Bar | 2.5Bar | Only Settable via Windows Software
15 | LLOP Sensor R6 |  | 67Ω | 0-999Ω | 67Ω | Only Settable via Windows Software
16 | LLOP Sensor V6 |  | 3Bar | 0.0-10.0 Bar | 3Bar | Only Settable via Windows Software
17 | LLOP Sensor R7 |  | 86Ω | 0-999Ω | 86Ω | Only Settable via Windows Software
18 | LLOP Sensor V7 |  | 4Bar | 0.0-10.0 Bar | 4Bar | Only Settable via Windows Software
19 | LLOP Sensor R8 |  | 105Ω | 0-999Ω | 105Ω | Only Settable via Windows Software
20 | LLOP Sensor V8 |  | 5Bar | 0.0-10.0 Bar | 5Bar | Only Settable via Windows Software
21 | LLOP Sensor R9 |  | 124Ω | 0-999Ω | 124Ω | Only Settable via Windows Software
22 | LLOP Sensor V9 |  | 6Bar | 0.0-10.0 Bar | 6Bar | Only Settable via Windows Software
23 | LLOP Sensor R10 |  | 143Ω | 0-999Ω | 143Ω | Only Settable via Windows Software
24 | LLOP Sensor V10 |  | 7Bar | 0.0-10.0 Bar | 7Bar | Only Settable via Windows Software
25 | Fuel Sensor | Select the installed sensor for Fuel The installed sensor should be Electronics or Linear if system suppliers as TMTL | .5-4.5(0-100%) | User Deﬁned Type A Sam-0 Sam-1 Electronics Linear 0-5V(0-100%) Disabled* | Electronics | Only Settable via Windows Software
26 | Fuel Sensor R1 | R1 to R10 = Resistance Value V1 to V10 = Corresponding fuel level in %. These table are used when sensor type is selected as user deﬁned. | 10Ω | 0-999Ω | 10Ω | Only Settable via Windows Software
27 | Fuel Sensor V1 |  | 0 | 0-100% | 0 | Only Settable via Windows Software
28 | Fuel Sensor R2 |  | 29Ω | 0-999Ω | 29Ω | Only Settable via Windows Software
29 | Fuel Sensor V2 |  | 0.1 | 0-100% | 10% | Only Settable via Windows Software
30 | Fuel Sensor R3 |  | 48Ω | 0-999Ω | 48Ω | Only Settable via Windows Software
31 | Fuel Sensor V3 |  | 0.2 | 0-100% | 20% | Only Settable via Windows Software
32 | Fuel Sensor R4 |  | 67Ω | 0-999Ω | 67Ω | Only Settable via Windows Software
33 | Fuel Sensor V4 |  | 0.3 | 0-100% | 30% | Only Settable via Windows Software
34 | Fuel Sensor R5 |  | 86Ω | 0-999Ω | 86Ω | Only Settable via Windows Software
35 | Fuel Sensor V5 |  | 0.4 | 0-100% | 40% | Only Settable via Windows Software
36 | Fuel Sensor R6 |  | 105Ω | 0-999Ω | 105Ω | Only Settable via Windows Software
37 | Fuel Sensor V6 |  | 0.5 | 0-100% | 50% | Only Settable via Windows Software
38 | Fuel Sensor R7 |  | 124Ω | 0-999Ω | 124Ω | Only Settable via Windows Software
39 | Fuel Sensor V7 |  | 0.6 | 0-100% | 60% | Only Settable via Windows Software
40 | Fuel Sensor R8 |  | 143Ω | 0-999Ω | 143Ω | Only Settable via Windows Software
41 | Fuel Sensor V8 |  | 0.7 | 0-100% | 70% | Only Settable via Windows Software
42 | Fuel Sensor R9 |  | 181Ω | 0-999Ω | 181Ω | Only Settable via Windows Software
43 | Fuel Sensor V9 |  | 0.9 | 0-100% | 90% | Only Settable via Windows Software
44 | Fuel Sensor R10 |  | 200Ω | 0-999Ω | 200Ω | Only Settable via Windows Software
45 | Fuel Sensor V10 |  | 100 | 0-100% | 100 | Only Settable via Windows Software
46 | Fuel Tank Capacity | The capacity of the fuel tank in litres. | 250 Ltr | Disabled 0-999Ltr | 250 Ltr | Only Settable via Windows Software
47 | HET Sensor | Select the installed sensor for HET The installed sensor should be either TMTL AIR 1C or TMTL AIR 3C or TMTL WATER if system suppliers as TMTL | TMTL Range 2 | User Deﬁned Type A M&M MNEPL VE TMTL RANGE 1 TMTL RANGE 2 TMTL WATER HUAFANG TATA GC(VDO) GC(MURPHY) Disabled * | TMTL RANGE 1 | Only Settable via Windows Software
48 | HET Sensor R1 | R1 to R10 = Resistance Value V1 to V10 = Corresponding temperature in °C. These table are used when sensor type is selected as user deﬁned. | 540Ω | 0-9999Ω | 540Ω | Only Settable via Windows Software
49 | HET Sensor V1 |  | 40℃ | 0-300 Celsius | 40℃ | Only Settable via Windows Software
50 | HET Sensor R2 |  | 458Ω | 0-9999Ω | 458Ω | Only Settable via Windows Software
51 | HET Sensor V2 |  | 45℃ | 0-300 Celsius | 45℃ | Only Settable via Windows Software
52 | HET Sensor R3 |  | 222Ω | 0-9999Ω | 222Ω | Only Settable via Windows Software
53 | HET Sensor V3 |  | 65℃ | 0-300 Celsius | 65℃ | Only Settable via Windows Software
54 | HET Sensor R4 |  | 120Ω | 0-9999Ω | 120Ω | Only Settable via Windows Software
55 | HET Sensor V4 |  | 85℃ | 0-300 Celsius | 85℃ | Only Settable via Windows Software
56 | HET Sensor R5 |  | 93Ω | 0-9999Ω | 93Ω | Only Settable via Windows Software
57 | HET Sensor V5 |  | 90℃ | 0-300 Celsius | 90℃ | Only Settable via Windows Software
58 | HET Sensor R6 |  | 80Ω | 0-9999Ω | 80Ω | Only Settable via Windows Software
59 | HET Sensor V6 |  | 95℃ | 0-300 Celsius | 95℃ | Only Settable via Windows Software
60 | HET Sensor R7 |  | 70Ω | 0-9999Ω | 70Ω | Only Settable via Windows Software
61 | HET Sensor V7 |  | 100℃ | 0-300 Celsius | 100℃ | Only Settable via Windows Software
62 | HET Sensor R8 |  | 60Ω | 0-9999Ω | 60Ω | Only Settable via Windows Software
63 | HET Sensor V8 |  | 105℃ | 0-300 Celsius | 105℃ | Only Settable via Windows Software
64 | HET Sensor R9 |  | 53Ω | 0-9999Ω | 53Ω | Only Settable via Windows Software
65 | HET Sensor V9 |  | 110℃ | 0-300 Celsius | 110℃ | Only Settable via Windows Software
66 | HET Sensor R10 |  | 46Ω | 0-9999Ω | 46Ω | Only Settable via Windows Software
67 | HET Sensor V10 |  | 115℃ | 0-300 Celsius | 115℃ | Only Settable via Windows Software
68 | Sensor Open | User can select the action to be taken in case of sensor open, it can be configured as a fault, or as warning | Disabled | Disabled * Warning | Disabled | Settable via Keypad on Controller or Windows Software
69 | CT Ratio | Current Transformer ratio | 1 | 1-100 | 15 | Only Settable via Windows Software
70 | Gen. RPM | Engine RPM Type | 1500 RPM | 1500RPM 3000RPM | 1500 RPM | Only Settable via Windows Software
71 | Contact ON Pin 32 | These are three programmable output which can be configured for any one function from the list | Heater/choke | None Unit Healthy Load Warning Fuel Pump Heater /Choke Pull Solenoid | Heater/choke | Only Settable via Windows Software
72 | Contact ON Pin 31 | These are three programmable output which can be conﬁgured for any one function from the list | None | None Unit Healthy Load Warning Fuel Pump Heater /Choke Pull Solenoid | None | Settable via Keypad on Controller or Windows Software
73 | Contact ON Pin 30 | These are three programmable output which can be conﬁgured for any one function from the list | None | None Unit Healthy Load Warning Fuel Pump Heater / Choke Pull Solenoid | None | Settable via Keypad on Controller or Windows Software
74 | Over Load KW | The Power(KW) above which the over load fault monitoring will start. The timer for it is over load delay. This fault is only enabled while the generator is running. On expiry of the timer the generator is stopped | 9.2 KW | 1.0-20.0 KW | 8.8 KW | Only Settable via Windows Software
75 | Over Current | The current above which the over current fault monitoring will start. The timer for it is over load delay. This fault is only enabled while the generator is running. On expiry of thetimer the generator is stopped | 50.1 A | 1.0-150 A | 48.0 A | Only Settable via Windows Software
76 | Over Load Delay | This is the timer for the over load condition either due to over KW or over current. On expiry of this timer the engine shall be stopped | 10 Sec | 1-15 Sec | 10 Sec | Only Settable via Windows Software
77 | High Load KW | The Power(KW) above which the High load fault monitoring will start. The timer for it is High load delay. This fault is only enabled while the generator is running. On expiry of the timer the generator is stopped | Disabled | Disabled* 1.0-150KW | 8KW | Only Settable via Windows Software
78 | High Load Delay | This is the timer for the High load Condition. On expiry of this timer the engine shall be stopped | 10 Sec | 1-9999Sec | 3600 Sec | Only Settable via Windows Software
79 | Reverse power | The Power(KW) above which the Res. Power fault monitoring will start. The timer for it is Res. Power delay. This fault is only enabled while the generator is running. On expiry of the timer the generator is stopped | Disabled | Disable* 0.5-150 KW | 0.5 | Settable via Keypad on Controller or Windows Software
80 | Reverse power delay | This is the timer for the Res. Power Condition. On expiry of this timer the engine shall be stopped | 10 Sec | 1-999 Sec | 1 Sec | Settable via Keypad on Controller or Windows Software
81 | Digital Input 1 | This can be conﬁgured for one out the listed below Parameters. RWL Oil Level Oil Temperature Canopy Temperature | RWL | RWL Oil Level Oil Temp. Canopy Temp. | RWL | Settable via Keypad on Controller or Windows Software
82 | Digital Input 1 Polarity | The polarity of digital input can be changed either normally open or normally close. | Normally open | Normally Open Normally Close | Normally open | Settable via Keypad on Controller or Windows Software
83 | Digital Input 2 | This can be configured for one out the listed below Parameters. LLOP Oil Level Oil Temperature Canopy Temperature | LLOP | LLOP Oil Level Oil Temp. Canopy Temp. | LLOP | Settable via Keypad on Controller or Windows Software
84 | Digital Input 2 Polarity | The polarity of digital input can be changed either normally open or normally close. | Normally open | Normally Open Normally Close | Normally open | Settable via Keypad on Controller or Windows Software
85 | Digital Input 3 | This can be configured for one out the listed below Parameters. Low Fuel Oil Level, Oil Temperature Canopy Temperature | Low Fuel | Low Fuel Oil Level Oil Temp. Canopy Temp. | Low Fuel | Only Settable via Windows Software
86 | Digital Input 3 Polarity | The polarity of digital input can be changed either normally open or normally close. | Normally open | Normally Open Normally Close | Normally open | Only Settable via Windows Software
87 | Digital Input 4 | This can be configured for one out the listed below Parameters. HET Oil Level Oil Temperature Canopy Temperature | HET/HWT | HET/HWT Oil Level Oil Temp. Canopy Temp. | HET/HWT | Settable via Keypad on Controller or Windows Software
88 | Digital Input 4 Polarity | The polarity of digital input can be changed either normally open or normally close. | Normally open | Normally Open Normally Close | Normally open | Settable via Keypad on Controller or Windows Software
89 | Digital Input 5 | This can be configured for one of the listed below Parameters. Canopy door open Oil Level Oil Temperature Canopy Temperature V- belt Ext-1 Ext-2 EGR Warning EGR Fault Padmini EGR | C Door open | C Door open V-belt Ext-1, Ext-2 EGR Warning EGR Fault Padmini EGR | EGR Fault | Settable via Keypad on Controller or Windows Software
90 | Digital Input 5 Polarity | The polarity of digital input can be changed either normally open or normally close. | Normally open | Normally Open Normally Close | Normally Close | Settable via Keypad on Controller or Windows Software
91 | Digital Input 6 | This can be configured for one of the listed below Parameters. Fire Oil Level Oil Temperature Canopy Temperature V- belt Ext-1 Ext-2 EGR Warning EGR Fault Padmini EGR | Fire | Fire Oil Level Oil Temp. Canopy Temp. V-belt Ext-1, Ext-2 EGR Warning EGR Fault Padmini EGR | EGR Warning | Settable via Keypad on Controller or Windows Software
92 | Digital Input 6 Polarity | The polarity of digital input can be changed either normally open or normally close. | Normally open | Normally Open Normally Close | Normally open | Settable via Keypad on Controller or Windows Software
93 | Digital Input 7 | This can be configured for one of the listed below Parameters. Half Fuel Warning Oil Level Oil Temperature Canopy Temperature V- belt Ext-1 Ext-2 EGR Warning EGR Fault Padmini EGR | Half Fuel Warning | Half Fuel Warning Oil Level Oil Temp. Canopy Temp. V-belt Ext-1, Ext-2 EGR Warning EGR Fault Padmini EGR | Half Fuel Warning | Only Settable via Windows Software
94 | Digital Input 7 Polarity | The polarity of digital input can be changed either normally open or normally close. | Normally open | Normally Open Normally Close | Normally open | Only Settable via Windows Software
95 | Digital Input 8 | This can be conﬁgured for one of the listed below Parameters. Oil Level Oil Temperature Canopy Temperature V-belt Ext-1 Ext-2 EGR Warning EGR Fault Padmini EGR | Canopy Temp. | Oil Level Oil Temp. Canopy Temp. V-belt Ext-1, Ext-2 EGR Warning EGR Fault Padmini EGR | Canopy Temp. | Settable via Keypad on Controller or Windows Software
96 | Digital Input 8 Polarity | The polarity of digital input can be changed either normally open or normally close. | Normally open | Normally Open Normally Close | Normally open | Settable via Keypad on Controller or Windows Software
97 | Fan high current | Maximum limit for fan | 1.1A | Disable* 0-3.5A | 1.1A | Only Settable via Windows Software
98 | Fan low current | Minimum Limit For fan current. This Parameter is disabled if the above paramters is disabled. | 0.2A | 0-3.5A | 0.2A | Only Settable via Windows Software
99 | Fan current delay | This is the timer for fan current trip. | 25 Sec | 1-60 Sec | 25 Sec | Only Settable via Windows Software
100 | Generator O/V | Max. Permissible Generator voltage, above this the Generator voltage is treated unhealthy & the Generator is stopped on voltage fault. | 285V | 150-300V | 265 V | Only Settable via Windows Software
101 | Generator U/V | Min. permissible Generator voltage, below this the Generator voltage is treated unhealthy & the Generator is stopped on voltage fault. | 185V | 100-300V | 190 V | Only Settable via Windows Software
102 | Gen Voltage Delay | Duration for which generator Over/Under voltage condition can be tolerated before stopping the Generator. | 10 Sec | 1-300 Sec | 10 Sec | Only Settable via Windows Software
103 | Generator Over Frq. | Max. Permissible Generator Frq., above this the Generator Frq. is treated unhealthy & the Generator is stopped on Frq. fault. | 55 Hz | 25-70Hz Disable* | 55 Hz | Only Settable via Windows Software
104 | Generator Under Frq. | Min. permissible Generator Frq., below this the Generator Frq. is treated unhealthy & the Generator isstopped Frq. fault. | 45 Hz | Disable* 25-70Hz | 45 Hz | Only Settable via Windows Software
105 | Gen Frq. Delay | Duration for which Generator Over /Under Frq. condition can be tolerated before stopping the Generator. This setting is not available if (4)&(5) are disabled | 5 sec | 1-300 Sec. | 5 Sec | Only Settable via Windows Software
106 | Current Unbalance | The maximum permissible current unbalance in %. The unbalance starts only after the system is loaded to 25%of its capacity | Disabled | 5-100% Disable | Disabled | Only Settable via Windows Software
107 | Current Unbalance Delay | Duration for which the current unbalance can be tolerated before triggering the fault | 10 Sec | 1-999Sec | 10 Sec | Only Settable via Windows Software
108 | Pickup Voltage | This parameter speciﬁes the generator voltage at which it is presumed to have started and crank has to be terminated | 30V | 30-150V | 30V | Only Settable via Windows Software
109 | Pick Up RPM | This parameter speciﬁes the edge RPM ( deﬁne for DG voltage) at which crank shall be terminated. | 300RPM | 300-1200 | 300RPM | Only Settable via Windows Software
110 | First Service Due Hr | Time, in hours, for next service due warning. | 500 | 1-999 Hrs | 50Hrs | Settable via Keypad on Controller or Windows Software
111 | Later service due hr | Time, in hours, for next service due warning. | 500 | 1-999 Hrs | 500Hrs | Settable via Keypad on Controller or Windows Software
112 | Crank Cut Method | Auto disconnects the crank command on detection of either voltage build-up/ voltage or oil pressure build up | Volt+Hz+Switch | Volt+Hz Volt+Hz+Switch Volt+Hz+Sensor Volt+Hz+Sensor+Switch | Volt+Hz+Switch | Only Settable via Windows Software
113 | Pick Up KVA | If the current level crosses this limit the contact is energized after the programmed supervision time | 8 KVA | 1-9999 KVA | 8 KVA | Only Settable via Windows Software
114 | Reset KVA | If the current level falls below this limit the contact is de-energized after the programmed supervision time. | 8 KVA | 1-9999 KVA | 8 KVA | Only Settable via Windows Software
115 | KVA Warning Delay | The supervision time for the above 2 parameters. | 5 Sec | 1-999 Sec | 5 Sec | Only Settable via Windows Software
116 | Choke Pre time | Keep the choke for this time before the engine has started. | Disabled | Disable* 1-999 Sec | Disabled | Settable via Keypad on Controller or Windows Software
117 | Choke Post time | Keep the choke for this time after the engine has started. | Disabled | Disable* 1-999 Sec | Disabled | Settable via Keypad on Controller or Windows Software
118 | Pump Pre Time | Activate the Pump by this time before cranking | 2 Sec | 1-999Sec | 2 Sec | Only Settable via Windows Software
119 | Generator Warmup Delay | The load is switched to Generator after expiry of this time | 0 Sec | 0-999Sec | 15 Sec | Settable via Keypad on Controller or Windows Software
120 | Generator Recooling Delay | The time for which the Generator is allowed to run on no load before switching off | 30 Sec | 0-999Sec | 30 Sec | Settable via Keypad on Controller or Windows Software
121 | Fuel Warn Level | Monitoring value of fuel level below which fuel level warning is generated. | 50% | Disable* 10-80 % | 50% | Only Settable via Windows Software
122 | Fuel Warn Delay | Monitoring time of fuel level after which fuel level warning is generated. | 10 Sec | 1-99 Sec | 10 Sec | Only Settable via Windows Software
123 | Fuel Trip Level | Monitoring value of fuel level below which fuel level trip is generated. | 15% | 10-81 % Disable | 15% | Only Settable via Windows Software
124 | Fuel Trip Delay | Monitoring time of fuel level after which fuel level trip is generated. | 10 Sec | 1-999 Sec | 10 Sec | Only Settable via Windows Software
125 | LLOP Trip Level | Monitoring value of lube oil pressure below which LLOP trip is generated. | 0.7 Kg/Cm2 | 0.3-8.5 Kg/cm2 Disable | 0.7 Kg/Cm2 | Only Settable via Windows Software
126 | LLOP Trip Delay | Monitoring time of lube oil pressure after which LLOP trip is generated. | 10 Sec | 0-999 Sec | 10 Sec | Only Settable via Windows Software
127 | HET Trip Level | Monitoring value of water temperature above which HET trip is generated. | Disabled | 40-251 Disabled* | Disabled | Only Settable via Windows Software
128 | HET Trip Delay | Monitoring time of water temperature after which HET trip is generated. | 10 Sec | 10-60 Sec | 10 Sec | Only Settable via Windows Software
129 | Digital Input 1 Delay | Delay for programmable digital input. Digital input are explained above. | 10 Sec | 1-99 Sec | 10 Sec | Settable via Keypad on Controller or Windows Software
130 | Digital Input 2 Delay | Delay for programmable digital input. Digital input are explained above. | 10 Sec | 1-99 Sec | 10 Sec | Settable via Keypad on Controller or Windows Software
131 | Digital Input 3 Delay | Delay for programmable digital input. Digital input are explained above. | 10 Sec | 1-99 Sec | 10 Sec | Only Settable via Windows Software
132 | Digital Input 4 Delay | Delay for programmable digital input. Digital input are explained above. | 10 Sec | 1-99 Sec | 10 Sec | Settable via Keypad on Controller or Windows Software
133 | Digital Input 5 Delay | Delay for programmable digital input. Digital input are explained above. | 10 Sec | 1-99 Sec | 10 Sec | Settable via Keypad on Controller or Windows Software
134 | Digital Input 6 Delay | Delay for programmable digital input. Digital input are explained above. | 10 Sec | 1-299 Sec | 10 Sec | Settable via Keypad on Controller or Windows Software
135 | Digital Input 7 Delay | Delay for programmable digital input. Digital input are explained above. | 10 Sec | 1-99 Sec | 10 Sec | Only Settable via Windows Software
136 | Digital Input 8 Delay | Delay for programmable digital input. Digital input are explained above. | 10 Sec | 1-99 Sec | 10 Sec | Settable via Keypad on Controller or Windows Software
137 | Chg Alt-V Belt Delay | Duration for which the V-Belt signal should be continuously deactive to be recognized as a fault and action initiated. This fault is only enabled while the generator is running. | 180 Sec | Disable* 1-299 Sec | Disable | Settable via Keypad on Controller or Windows Software
138 | Hooter ON Time | Duration for which the hooter shall be ON, if not externally reset, while announcing a fault. | 30 Sec | 1-299 Sec | 30 Sec | Settable via Keypad on Controller or Windows Software
139 | Crank ON Time | Maximum crank time | 2.0 Sec | 0.5-20 Sec | 2.0 Sec | Settable via Keypad on Controller or Windows Software
140 | Crank Gap Time | The delay between two successive cranks | 10 Sec | 1-99 Sec | 10 Sec | Settable via Keypad on Controller or Windows Software
141 | Crank Attempts | The maximum number of cranks that shall be issued to start the Engine | 3 | 3-5 | 3 | Settable via Keypad on Controller or Windows Software
142 | Solenoid ON time | The time for which stop solenoid will be kept active while stopping the engine | 35 Sec | 1-99 Sec | 35 Sec | Settable via Keypad on Controller or Windows Software
143 | Disp Auto Scroll | Setting ON will enable Auto Scroll of display. OFF: No scroll and next parameter can be viewed by pressing next switch | ON | ON/OFF | ON | Settable via Keypad on Controller or Windows Software
144 | Scrolling Delay | After this duration next parameter Displayed on Display. | 10 Sec | 5-99Sec | 10 Sec | Settable via Keypad on Controller or Windows Software
145 | Battery UV Warning | Min. permissible battery voltage, below this the voltage is treated unhealthy & warning is generated. | 10.0 V | Disabled* 7.9-12V | 10.0 V | Settable via Keypad on Controller or Windows Software
146 | Battery OV Warning | Max. permissible battery voltage, above this the voltage is treated unhealthy & warning is generated. | 14.5 V | 12-30V Disabled* | 16.5 V | Settable via Keypad on Controller or Windows Software
147 | Canopy Over Temp. | Monitoring value of Canopy Temp. Above which Canopy temp. Is generated. | 27.0 Celsius | 15.0-99.9 Celsius | 60 deg Celsius | Settable via Keypad on Controller or Windows Software
148 | Canopy Over Temp. Delay | Monitoring Time value of Canopy Temp. After which Canopy temp. Is generated. | 20 sec | 1-999Sec | 20 sec | Settable via Keypad on Controller or Windows Software
149 | NCD Strategy | Enable or Disable NCD (NOx Control Diagnostic) System as per CPCB4+ guidelines | Disabled* | Disabled* Enabled | Disabled* | Settable via Keypad on Controller or Windows Software
150 | NCD Warn Hrs | Set the time in Hrs while Generator is running after which NCD Warning will get activated if any EGR warning remains in the system during this whole period. | 36.00 Hrs | 0.01-99.99 Hrs | 36.00 Hrs | Settable via Keypad on Controller or Windows Software
151 | NCD Fault Hrs | Set the time in Hrs while Generator is running after which NCD Fault will get activated if any EGR warning remains in the system during this whole period. | 72.00 Hrs | 0.01-99.99 Hrs | 72.00 Hrs | Settable via Keypad on Controller or Windows Software
152 | NCD Heal Hrs | Set the time in Hrs while Generator is running after which NCD Error timer will get reset if no EGR warning remains in the system during this whole period. | 40.00 Hrs | 0.01-99.99 Hrs | 40.00 Hrs | Settable via Keypad on Controller or Windows Software
153 | Ann. DG On | Selected contact is activated if Generator is on | No Annuciation | No Annunciation Contact on pin 1-12 | On Contact 1 | Settable via Keypad on Controller or Windows Software
154 | Ann. DG Off | Selected contact is activated if Generator is off. | No Annuciation | No Annunciation Contact on pin 1-12 | No Annuciation | Settable via Keypad on Controller or Windows Software
155 | Ann. DG On Load | Selected contact is activated if Generator is On load | On Contact 7 | No Annunciation Contact on pin 1-12 | On Contact 2 | Settable via Keypad on Controller or Windows Software
156 | Ann. Unit OK | Selected contact is activated if unit is ok. | No Annuciation | No Annunciation Contact on pin 1-12 | No Annuciation | Settable via Keypad on Controller or Windows Software
157 | Ann. Fuel Trip | Selected contact is activated if fuel fault registered | On Contact 10 | No Annunciation Contact on pin 1-12 | No Annuciation | Settable via Keypad on Controller or Windows Software
158 | Ann. LLOP Trip | Selected contact is activated if LLOP fault registered | On Contact 1 | No Annunciation Contact on pin 1-12 | On Contact 5 | Settable via Keypad on Controller or Windows Software
159 | Ann. HET Trip | Selected contact is activated if HET fault registered. | On Contact 2 | No Annunciation Contact on pin 1-12 | On Contact 8 | Settable via Keypad on Controller or Windows Software
160 | Ann. DG Voltage | Selected contact is activated if Generator voltage is healthy. | No Annuciation | No Annunciation Contact on pin 1-12 | No Annuciation | Settable via Keypad on Controller or Windows Software
161 | Ann. Emergency | Selected contact is activated if emergency fault is registered. | No Annuciation | No Annunciation Contact on pin 1-12 | No Annuciation | Settable via Keypad on Controller or Windows Software
162 | Ann. DG Overload | Selected contact is activated if generator is overloaded. | On Contact 3 | No Annunciation Contact on pin 1-12 | On Contact 3 | Settable via Keypad on Controller or Windows Software
163 | Ann. DG High Load | Selected contact is activated if generator is highloaded. | No Annuciation | No Annunciation Contact on pin 1-12 | No Annuciation | Settable via Keypad on Controller or Windows Software
164 | Ann. DG Frequency | Selected contact is activated if generator over frequency/under frequency fault registered | On Contact 5 | No Annunciation Contact on pin 1-12 | No Annunciation | Settable via Keypad on Controller or Windows Software
165 | Ann. RWL Fault | Selected contact is activated if RWL fault registered. | On Contact 8 | No Annunciation Contact on pin 1-12 | No Annunciation | Settable via Keypad on Controller or Windows Software
166 | Ann. Charging alternator/ V-belt | Selected contact is activated if Charging alternator/V-belt fault registered. | On Contact 6 | No Annunciation Contact on pin 1-12 | No Annunciation | Settable via Keypad on Controller or Windows Software
167 | Ann. Fail to Start | Selected contact is activated if Fail to Start fault registered. | On Contact 11 | No Annunciation Contact on pin 1-12 | On Contact 11 | Settable via Keypad on Controller or Windows Software
168 | Ann. Fail to stop | Selected contact is activated if Fail to stop fault registered. | On Contact 12 | No Annunciation Contact on pin 1-12 | On Contact 12 | Settable via Keypad on Controller or Windows Software
169 | Ann. Current Unbalance | Selected contact is activated if Current Unbalance fault registered. | No Annunciation | No Annunciation Contact on pin 1-12 | No Annunciation | Settable via Keypad on Controller or Windows Software
170 | Ann. Fuel Open | Selected contact is activated if fuel sensor is open. | No Annunciation | No Annunciation Contact on pin 1-12 | No Annunciation | Settable via Keypad on Controller or Windows Software
171 | Ann. LLOP Open | Selected contact is activated if LLOP sensor is open. | No Annunciation | No Annunciation Contact on pin 1-12 | No Annunciation | Settable via Keypad on Controller or Windows Software
172 | Ann. HET Open | Selected contact is activated if HET sensor is open. | No Annunciation | No Annunciation Contact on pin 1-12 | No Annunciation | Settable via Keypad on Controller or Windows Software
173 | Ann. Canopy Temperature | Selected contact is activated if Canopy Temperature is high. | No Annunciation | No Annunciation Contact on pin 1-12 | No Annunciation | Settable via Keypad on Controller or Windows Software
174 | Ann. Fire | Selected contact is activated if ﬁre fault registered. | No Annunciation | No Annunciation Contact on pin 1-12 | No Annunciation | Settable via Keypad on Controller or Windows Software
175 | Ann. Oil Temperature | Selected contact is activated if Oil Temperature is high | No Annunciation | No Annunciation Contact on pin 1-12 | No Annunciation | Settable via Keypad on Controller or Windows Software
176 | Ann. Oil level | Selected contact is activated if Oil level is low. | No Annunciation | No Annunciation Contact on pin 1-12 | No Annunciation | Settable via Keypad on Controller or Windows Software
177 | Ann. Service Due | Selected contact is activated if Service is due. | No Annunciation | No Annunciation Contact on pin 1-12 | No Annunciation | Settable via Keypad on Controller or Windows Software
178 | Ann. Battery NOK | Selected contact is activated if battery voltage is unhealthy | No Annunciation | No Annunciation Contact on pin 1-12 | No Annunciation | Settable via Keypad on Controller or Windows Software
179 | Ann. common Fault | Selected contact is activated if generator stopped on any fault | On Contact 4 | No Annunciation Contact on pin 1-12 | On Contact 4 | Settable via Keypad on Controller or Windows Software
180 | Ann. Half Fuel Warning | Selected contact is activated if low fuel warning is generated | On Contact 9 | No Annunciation Contact on pin 1-12 | On Contact 9 | Settable via Keypad on Controller or Windows Software
181 | Ann. C Door Open | Selected contact is activated if Canopy Door is opened | No Annunciation | No Annunciation Contact on pin 1-12 | No Annunciation | Settable via Keypad on Controller or Windows Software
182 | Ann. Gen. Rev. power | Selected contact is activated if Res. Power High | No Annunciation | No Annunciation Contact on pin 1-12 | No Annunciation | Settable via Keypad on Controller or Windows Software
183 | Ann. EGR Warn | Selected contact is activated if any EGR Warning is active | No Annunciation | No Annunciation Contact on pin 1-12 | No Annunciation | Settable via Keypad on Controller or Windows Software
184 | Ann. NCD Warn | Selected contact is activated if NCD Warning is active | No Annunciation | No Annunciation Contact on pin 1-12 | No Annunciation | Settable via Keypad on Controller or Windows Software
185 | Ann. NCD Fault | Selected contact is activated if NCD Fault is active | No Annunciation | No Annunciation Contact on pin 1-12 | No Annunciation | Settable via Keypad on Controller or Windows Software
186 | Ann. CPCB4+ Audio | Selected contact is activated according to CPCB4+ Audio indication requirements (Active every 5 seconds for 2 seconds when NCD Warning active and Active every 2 seconds for 2 seconds when NCD Fault is acive other wise not active) | No Annunciation | No Annunciation Contact on pin 1-12 | No Annunciation | Settable via Keypad on Controller or Windows Software
187 | Device Id | Mod bus device ID | 1 | 1-247 | 1 | Settable via Keypad on Controller or Windows Software
188 | Baud Rate | RS 485 Communication Baud rate | 9600 | 1200 2400 4800 9600 19200 | 9600 | Settable via Keypad on Controller or Windows Software
189 | Parity | RS 485 Communication Parity Bits | None | Even Odd None | None | Settable via Keypad on Controller or Windows Software
190 | Stop Bit | RS 485 Communication Stop Bits | 1 | 1 2 | 1 | Settable via Keypad on Controller or Windows Software

## Setting-M&M-15KVA (hidden)
| Controller: | ECON-MAN-IND
| Firmware | v2.06
No. | Name Of Setting On LCD Display | Setting Description | Default setting | Setting Range | Default setting for 15KVA M&M Genset | Remarks | Edit Options
1 | Suppliers | Company logo and default parameter is set as per system suppliers. | Procom | PROCOM TMTL M&M | M&M |  | Only Settable via Windows Software
2 | System Conﬁg | ECON provides complete ﬂexibility in system designing; it is possible to select manual operation for DG phases. | Generator 3 Phase | Generator 1 Phase Generator 3 Phase | Generator 1 Phase |  | Settable via Keypad on Controller or Windows Software
3 | Solenoid Type | Pull To Start In this mode fuel solenoid contact changes from Open to Close at the time of cranking and remains close till the gen set is running. For stopping the generator this contact opens. Pull To Stop In this mode fuel solenoid contact remains open at the time of cranking and till the gen set is running. For stopping the generator this contact closes for a user programmed time. | Pull To Stop | Pull to Stop Pull to Start | Pull To Stop |  | Only Settable via Windows Software
4 | LLOP Sensor Type | Select the installed sensor for LLOP | TMTL | User Deﬁned Type A M&M MNEPL VE TMTL HUAFANG TATA GC(VDO) GC(MURPHY) 4-20MA M&M-2 Disabled * | User Deﬁned |  | Only Settable via Windows Software
5 | LLOP Sensor R1 | R1 to R10 = Resistance Value V1 to V10 = Corresponding pressure value. These table are used when sensor type is selected as user deﬁned. | 10Ω | 0-999Ω | 10Ω |  | Only Settable via Windows Software
6 | LLOP Sensor V1 |  | 0 Bar | 0.0-10.0 Bar | 0 Bar |  | Only Settable via Windows Software
7 | LLOP Sensor R2 |  | 29Ω | 0-999Ω | 30Ω |  | Only Settable via Windows Software
8 | LLOP Sensor V2 |  | 1 Bar | 0.0-10.0 Bar | 1 Bar |  | Only Settable via Windows Software
9 | LLOP Sensor R3 |  | 38Ω | 0-999Ω | 40Ω |  | Only Settable via Windows Software
10 | LLOP Sensor V3 |  | 1.5Bar | 0.0-10.0 Bar | 2 Bar |  | Only Settable via Windows Software
11 | LLOP Sensor R4 |  | 48Ω | 0-999Ω | 64Ω |  | Only Settable via Windows Software
12 | LLOP Sensor V4 |  | 2Bar | 0.0-10.0 Bar | 3 Bar |  | Only Settable via Windows Software
13 | LLOP Sensor R5 |  | 57Ω | 0-999Ω | 80Ω |  | Only Settable via Windows Software
14 | LLOP Sensor V5 |  | 2.5Bar | 0.0-10.0 Bar | 4 Bar |  | Only Settable via Windows Software
15 | LLOP Sensor R6 |  | 67Ω | 0-999Ω | 96Ω |  | Only Settable via Windows Software
16 | LLOP Sensor V6 |  | 3Bar | 0.0-10.0 Bar | 5 Bar |  | Only Settable via Windows Software
17 | LLOP Sensor R7 |  | 86Ω | 0-999Ω | 96Ω |  | Only Settable via Windows Software
18 | LLOP Sensor V7 |  | 4Bar | 0.0-10.0 Bar | 5 Bar |  | Only Settable via Windows Software
19 | LLOP Sensor R8 |  | 105Ω | 0-999Ω | 96Ω |  | Only Settable via Windows Software
20 | LLOP Sensor V8 |  | 5Bar | 0.0-10.0 Bar | 5 Bar |  | Only Settable via Windows Software
21 | LLOP Sensor R9 |  | 124Ω | 0-999Ω | 96Ω |  | Only Settable via Windows Software
22 | LLOP Sensor V9 |  | 6Bar | 0.0-10.0 Bar | 5 Bar |  | Only Settable via Windows Software
23 | LLOP Sensor R10 |  | 143Ω | 0-999Ω | 96Ω |  | Only Settable via Windows Software
24 | LLOP Sensor V10 |  | 7Bar | 0.0-10.0 Bar | 5 Bar |  | Only Settable via Windows Software
25 | Fuel Sensor | Select the installed sensor for Fuel The installed sensor should be Electronics or Linear if system suppliers as TMTL | 0.5-4.5V(0-100%) | User Deﬁned Type A Sam-0 Sam-1 Electronics Linear 0-5V(0-100%) Disabled* | User Deﬁned |  | Only Settable via Windows Software
26 | Fuel Sensor R1 | R1 to R10 = Resistance Value V1 to V10 = Corresponding fuel level in %. These table are used when sensor type is selected as user deﬁned. | 10Ω | 0-999Ω | 14Ω |  | Only Settable via Windows Software
27 | Fuel Sensor V1 |  | 0 | 0-100% | 0% |  | Only Settable via Windows Software
28 | Fuel Sensor R2 |  | 29Ω | 0-999Ω | 22Ω |  | Only Settable via Windows Software
29 | Fuel Sensor V2 |  | 0.1 | 0-100% | 10% |  | Only Settable via Windows Software
30 | Fuel Sensor R3 |  | 48Ω | 0-999Ω | 37Ω |  | Only Settable via Windows Software
31 | Fuel Sensor V3 |  | 0.2 | 0-100% | 20% |  | Only Settable via Windows Software
32 | Fuel Sensor R4 |  | 67Ω | 0-999Ω | 74Ω |  | Only Settable via Windows Software
33 | Fuel Sensor V4 |  | 0.3 | 0-100% | 30% |  | Only Settable via Windows Software
34 | Fuel Sensor R5 |  | 86Ω | 0-999Ω | 110Ω |  | Only Settable via Windows Software
35 | Fuel Sensor V5 |  | 0.4 | 0-100% | 40% |  | Only Settable via Windows Software
36 | Fuel Sensor R6 |  | 105Ω | 0-999Ω | 139Ω |  | Only Settable via Windows Software
37 | Fuel Sensor V6 |  | 0.5 | 0-100% | 50% |  | Only Settable via Windows Software
38 | Fuel Sensor R7 |  | 124Ω | 0-999Ω | 159Ω |  | Only Settable via Windows Software
39 | Fuel Sensor V7 |  | 0.6 | 0-100% | 60% |  | Only Settable via Windows Software
40 | Fuel Sensor R8 |  | 143Ω | 0-999Ω | 171Ω |  | Only Settable via Windows Software
41 | Fuel Sensor V8 |  | 0.7 | 0-100% | 70% |  | Only Settable via Windows Software
42 | Fuel Sensor R9 |  | 181Ω | 0-999Ω | 174Ω |  | Only Settable via Windows Software
43 | Fuel Sensor V9 |  | 0.9 | 0-100% | 80% |  | Only Settable via Windows Software
44 | Fuel Sensor R10 |  | 200Ω | 0-999Ω | 184Ω |  | Only Settable via Windows Software
45 | Fuel Sensor V10 |  | 100 | 0-100% | 100% |  | Only Settable via Windows Software
46 | Fuel Tank Capacity | The capacity of the fuel tank in litres. | 250 Ltr | Disabled 0-999Ltr | 250 Ltr |  | Only Settable via Windows Software
47 |  | Select the installed sensor for HET The installed sensor should be either TMTL AIR 1C or TMTL AIR 3C or TMTL WATER if system suppliers as TMTL | TMTL Range 2 | User Deﬁned Type A M&M MNEPL VE TMTL RANGE 1 TMTL RANGE 2 TMTL WATER HUAFANG TATA GC(VDO) GC(MURPHY) Disabled * | User Deﬁned | Same setting for either HET/HWT | Only Settable via Windows Software
48 | HET Sensor R1 | R1 to R10 = Resistance Value V1 to V10 = Corresponding temperature in °C. These table are used when sensor type is selected as user deﬁned. | 540Ω | 0-9999Ω | 35Ω | Same setting for either HET/HWT | Only Settable via Windows Software
49 | HET Sensor V1 |  | 40℃ | 0-300 Celsius | 125℃ | Same setting for either HET/HWT | Only Settable via Windows Software
50 | HET Sensor R2 |  | 458Ω | 0-9999Ω | 50Ω | Same setting for either HET/HWT | Only Settable via Windows Software
51 | HET Sensor V2 |  | 45℃ | 0-300 Celsius | 110℃ | Same setting for either HET/HWT | Only Settable via Windows Software
52 | HET Sensor R3 |  | 222Ω | 0-9999Ω | 70Ω | Same setting for either HET/HWT | Only Settable via Windows Software
53 | HET Sensor V3 |  | 65℃ | 0-300 Celsius | 100℃ | Same setting for either HET/HWT | Only Settable via Windows Software
54 | HET Sensor R4 |  | 120Ω | 0-9999Ω | 93Ω | Same setting for either HET/HWT | Only Settable via Windows Software
55 | HET Sensor V4 |  | 85℃ | 0-300 Celsius | 90℃ | Same setting for either HET/HWT | Only Settable via Windows Software
56 | HET Sensor R5 |  | 93Ω | 0-9999Ω | 120Ω | Same setting for either HET/HWT | Only Settable via Windows Software
57 | HET Sensor V5 |  | 90℃ | 0-300 Celsius | 85℃ | Same setting for either HET/HWT | Only Settable via Windows Software
58 | HET Sensor R6 |  | 80Ω | 0-9999Ω | 220Ω | Same setting for either HET/HWT | Only Settable via Windows Software
59 | HET Sensor V6 |  | 95℃ | 0-300 Celsius | 65℃ | Same setting for either HET/HWT | Only Settable via Windows Software
60 | HET Sensor R7 |  | 70Ω | 0-9999Ω | 458Ω | Same setting for either HET/HWT | Only Settable via Windows Software
61 | HET Sensor V7 |  | 100℃ | 0-300 Celsius | 45℃ | Same setting for either HET/HWT | Only Settable via Windows Software
62 | HET Sensor R8 |  | 60Ω | 0-9999Ω | 700Ω | Same setting for either HET/HWT | Only Settable via Windows Software
63 | HET Sensor V8 |  | 105℃ | 0-300 Celsius | 35℃ | Same setting for either HET/HWT | Only Settable via Windows Software
64 | HET Sensor R9 |  | 53Ω | 0-9999Ω | 850Ω | Same setting for either HET/HWT | Only Settable via Windows Software
65 | HET Sensor V9 |  | 110℃ | 0-300 Celsius | 35℃ | Same setting for either HET/HWT | Only Settable via Windows Software
66 | HET Sensor R10 |  | 46Ω | 0-9999Ω | 1000Ω | Same setting for either HET/HWT | Only Settable via Windows Software
67 | HET Sensor V10 |  | 115℃ | 0-300 Celsius | 35℃ | Same setting for either HET/HWT | Only Settable via Windows Software
68 | Sensor Open | User can select the action to be taken in case of sensor open, it can be configured as a fault, or as warning | Disabled | Disabled * Warning | Warning |  | Settable via Keypad on Controller or Windows Software
69 | CT Ratio | Current Transformer ratio | 1 | 1-100 | 15 |  | Only Settable via Windows Software
70 | Gen. RPM | Engine RPM Type | 1500 RPM | 1500RPM 3000RPM | 1500 RPM |  | Only Settable via Windows Software
71 | Contact ON Pin 32 | These are three programmable output which can be configured for any one function from the list | Heater/choke | None Unit Healthy Load Warning Fuel Pump Heater /Choke Pull Solenoid | Fuel Pump |  | Only Settable via Windows Software
72 | Contact ON Pin 31 | These are three programmable output which can be conﬁgured for any one function from the list | None | None Unit Healthy Load Warning Fuel Pump Heater /Choke Pull Solenoid | None |  | Settable via Keypad on Controller or Windows Software
73 | Contact ON Pin 30 | These are three programmable output which can be conﬁgured for any one function from the list | None | None Unit Healthy Load Warning Fuel Pump Heater / Choke Pull Solenoid | None |  | Settable via Keypad on Controller or Windows Software
74 | Over Load KW | The Power(KW) above which the over load fault monitoring will start. The timer for it is over load delay. This fault is only enabled while the generator is running. On expiry of the timer the generator is stopped | 9.2 KW | 1.0-20.0 KW | 13.4 A |  | Only Settable via Windows Software
75 | Over Current | The current above which the over current fault monitoring will start. The timer for it is over load delay. This fault is only enabled while the generator is running. On expiry of thetimer the generator is stopped | 50.1 A | 1.0-150 A | 72 A |  | Only Settable via Windows Software
76 | Over Load Delay | This is the timer for the over load condition either due to over KW or over current. On expiry of this timer the engine shall be stopped | 10 Sec | 1-15 Sec | 15 Sec |  | Only Settable via Windows Software
77 | High load KW | The Power(KW) above which the High load fault monitoring will start. The timer for it is High load delay. This fault is only enabled while the generator is running. On expiry of the timer the generator is stopped | Disabled | Disabled* 1.0-150KW | 12.1 KW |  | Only Settable via Windows Software
78 | High delay | This is the timer for the High load Condition. On expiry of this timer the engine shall be stopped | 10 Sec | 1-9999Sec | 3600 Sec |  | Only Settable via Windows Software
79 | Reverse power | The Power(KW) above which the Res. Power fault monitoring will start. The timer for it is Res. Power delay. This fault is only enabled while the generator is running. On expiry of the timer the generator is stopped | Disabled | Disable* 0.5-150 KW | Disabled |  | Settable via Keypad on Controller or Windows Software
80 | Reverse power delay | This is the timer for the Res. Power Condition. On expiry of this timer the engine shall be stopped | 10 Sec | 1-999 Sec | 10 Sec | NA as Reverse Power Feature Disabled | Settable via Keypad on Controller or Windows Software
81 | Digital Input 1 | This can be conﬁgured for one out the listed below Parameters. RWL Oil Level Oil Temperature Canopy Temperature | RWL | RWL Oil Level Oil Temp. Canopy Temp. | RWL |  | Settable via Keypad on Controller or Windows Software
82 | Digital Input 1 Polarity | The polarity of digital input can be changed either normally open or normally close. | Normally open | Normally Open Normally Close | Normally open |  | Settable via Keypad on Controller or Windows Software
83 | Digital Input 2 | This can be configured for one out the listed below Parameters. LLOP Oil Level Oil Temperature Canopy Temperature | LLOP | LLOP Oil Level Oil Temp. Canopy Temp. | LLOP |  | Settable via Keypad on Controller or Windows Software
84 | Digital Input 2 Polarity | The polarity of digital input can be changed either normally open or normally close. | Normally open | Normally Open Normally Close | Normally open |  | Settable via Keypad on Controller or Windows Software
85 | Digital Input 3 | This can be configured for one out the listed below Parameters. Low Fuel Oil Level, Oil Temperature Canopy Temperature | Low Fuel | Low Fuel Oil Level Oil Temp. Canopy Temp. | Low Fuel |  | Only Settable via Windows Software
86 | Digital Input 3 Polarity | The polarity of digital input can be changed either normally open or normally close. | Normally open | Normally Open Normally Close | Normally open |  | Only Settable via Windows Software
87 | Digital Input 4 | This can be configured for one out the listed below Parameters. HET Oil Level Oil Temperature Canopy Temperature | HET/HWT | HET/HWT Oil Level Oil Temp. Canopy Temp. | HET/HWT |  | Settable via Keypad on Controller or Windows Software
88 | Digital Input 4 Polarity | The polarity of digital input can be changed either normally open or normally close. | Normally open | Normally Open Normally Close | Normally open |  | Settable via Keypad on Controller or Windows Software
89 | Digital Input 5 | This can be configured for one of the listed below Parameters. Canopy door open Oil Level Oil Temperature Canopy Temperature V- belt Ext-1 Ext-2 EGR Warning EGR Fault Padmini EGR | C Door open | C Door open V-belt Ext-1, Ext-2 EGR Warning EGR Fault Padmini EGR | C Door open |  | Settable via Keypad on Controller or Windows Software
90 | Digital Input 5 Polarity | The polarity of digital input can be changed either normally open or normally close. | Normally open | Normally Open Normally Close | Normally Open |  | Settable via Keypad on Controller or Windows Software
91 | Digital Input 6 | This can be configured for one of the listed below Parameters. Fire Oil Level Oil Temperature Canopy Temperature V- belt Ext-1 Ext-2 EGR Warning EGR Fault Padmini EGR | Fire | Fire Oil Level Oil Temp. Canopy Temp. V-belt Ext-1, Ext-2 EGR Warning EGR Fault Padmini EGR | Padmini EGR |  | Settable via Keypad on Controller or Windows Software
92 | Digital Input 6 Polarity | The polarity of digital input can be changed either normally open or normally close. | Normally open | Normally Open Normally Close | Normally Open |  | Settable via Keypad on Controller or Windows Software
93 | Digital Input 7 | This can be configured for one of the listed below Parameters. Half Fuel Warning Oil Level Oil Temperature Canopy Temperature V- belt Ext-1 Ext-2 EGR Warning EGR Fault Padmini EGR | Half Fuel Warning | Half Fuel Warning Oil Level Oil Temp. Canopy Temp. V-belt Ext-1, Ext-2 EGR Warning EGR Fault Padmini EGR | Half Fuel Warning |  | Only Settable via Windows Software
94 | Digital Input 7 Polarity | The polarity of digital input can be changed either normally open or normally close. | Normally open | Normally Open Normally Close | Normally open |  | Only Settable via Windows Software
95 | Digital Input 8 | This can be conﬁgured for one of the listed below Parameters. Oil Level Oil Temperature Canopy Temperature V-belt Ext-1 Ext-2 EGR Warning EGR Fault Padmini EGR | Canopy Temp. | Oil Level Oil Temp. Canopy Temp. V-belt Ext-1, Ext-2 EGR Warning EGR Fault Padmini EGR | Canopy Temp. |  | Settable via Keypad on Controller or Windows Software
96 | Digital Input 8 Polarity | The polarity of digital input can be changed either normally open or normally close. | Normally open | Normally Open Normally Close | Normally open |  | Settable via Keypad on Controller or Windows Software
97 | Fan high current | Maximum limit for fan | 1.1A | Disable* 0-3.5A | Disable* |  | Only Settable via Windows Software
98 | Fan low current | Minimum Limit For fan current. This Parameter is disabled if the above paramters is disabled. | 0.2A | 0-3.5A | 0.2A | NA as Fan Current Feature Disabled | Only Settable via Windows Software
99 | Fan current delay | This is the timer for fan current trip. | 25 Sec | 1-60 Sec | 25 Sec | NA as Fan Current Feature Disabled | Only Settable via Windows Software
100 | Generator O/V | Max. Permissible Generator voltage, above this the Generator voltage is treated unhealthy & the Generator is stopped on voltage fault. | 285V | 150-300V | 285V |  | Only Settable via Windows Software
101 | Generator U/V | Min. permissible Generator voltage, below this the Generator voltage is treated unhealthy & the Generator is stopped on voltage fault. | 185V | 100-300V | 185V |  | Only Settable via Windows Software
102 | Gen Voltage Delay | Duration for which generator Over/Under voltage condition can be tolerated before stopping the Generator. | 10 Sec | 1-300 Sec | 10 Sec |  | Only Settable via Windows Software
103 | Generator Over Frq. | Max. Permissible Generator Frq., above this the Generator Frq. is treated unhealthy & the Generator is stopped on Frq. fault. | 55 Hz | 25-70Hz Disable* | 55 Hz |  | Only Settable via Windows Software
104 | Generator Under Frq. | Min. permissible Generator Frq., below this the Generator Frq. is treated unhealthy & the Generator isstopped Frq. fault. | 45 Hz | Disable* 25-70Hz | 45 Hz |  | Only Settable via Windows Software
105 | Gen Frq. Delay | Duration for which Generator Over /Under Frq. condition can be tolerated before stopping the Generator. This setting is not available if (4)&(5) are disabled | 5 sec | 1-300 Sec. | 5 sec |  | Only Settable via Windows Software
106 | Current Unbalance | The maximum permissible current unbalance in %. The unbalance starts only after the system is loaded to 25%of its capacity | Disabled | 5-100% Disable | Disabled |  | Only Settable via Windows Software
107 | Current Unbalance Delay | Duration for which the current unbalance can be tolerated before triggering the fault | 10 Sec | 1-999Sec | 10 Sec | NA as Current Unbalanced Feature Disabled | Only Settable via Windows Software
108 | Pickup Voltage | This parameter speciﬁes the generator voltage at which it is presumed to have started and crank has to be terminated | 30V | 30-150V | 100V |  | Only Settable via Windows Software
109 | Pick Up RPM | This parameter speciﬁes the edge RPM ( deﬁne for DG voltage) at which crank shall be terminated. | 300RPM | 300-1200 | 600RPM |  | Only Settable via Windows Software
110 | First Service Due Hr | Time, in hours, for next service due warning. | 500 | 1-999 Hrs | 500 |  | Settable via Keypad on Controller or Windows Software
111 | Later service due hr | Time, in hours, for next service due warning. | 500 | 1-999 Hrs | 500 |  | Settable via Keypad on Controller or Windows Software
112 | Crank Cut Method | Auto disconnects the crank command on detection of either voltage build-up/ voltage or oil pressure build up | Volt+Hz+Switch | Volt+Hz Volt+Hz+Switch Volt+Hz+Sensor Volt+Hz+Sensor+Switch | Volt+Hz+Sensor |  | Only Settable via Windows Software
113 | Pick Up KVA | If the current level crosses this limit the contact is energized after the programmed supervision time | 8 KVA | 1-9999 KVA | 8 KVA | NA as Load Warning Feature not used | Only Settable via Windows Software
114 | Reset KVA | If the current level falls below this limit the contact is de-energized after the programmed supervision time. | 8 KVA | 1-9999 KVA | 8 KVA | NA as Load Warning Feature not used | Only Settable via Windows Software
115 | KVA Warning Delay | The supervision time for the above 2 parameters. | 5 Sec | 1-999 Sec | 5 Sec | NA as Load Warning Feature not used | Only Settable via Windows Software
116 | Choke Pre time | Keep the choke for this time before the engine has started. | Disabled | Disable* 1-999 Sec | Disabled |  | Settable via Keypad on Controller or Windows Software
117 | Choke Post time | Keep the choke for this time after the engine has started. | Disabled | Disable* 1-999 Sec | Disabled |  | Settable via Keypad on Controller or Windows Software
118 | Pump Pre Time | Activate the Pump by this time before cranking | 2 Sec | 1-999Sec | 2 Sec |  | Only Settable via Windows Software
119 | Generator Warmup Delay | The load is switched to Generator after expiry of this time | 0 Sec | 0-999Sec | 5 Sec |  | Settable via Keypad on Controller or Windows Software
120 | Generator Recooling Delay | The time for which the Generator is allowed to run on no load before switching off | 30 Sec | 0-999Sec | 30 Sec |  | Settable via Keypad on Controller or Windows Software
121 | Fuel Warn Level | Monitoring value of fuel level below which fuel level warning is generated. | 50% | Disable* 10-80 % | 40% |  | Only Settable via Windows Software
122 | Fuel Warn Delay | Monitoring time of fuel level after which fuel level warning is generated. | 10 Sec | 1-99 Sec | 10 Sec |  | Only Settable via Windows Software
123 | Fuel Trip Level | Monitoring value of fuel level below which fuel level trip is generated. | 15% | 10-81 % Disable | 15% |  | Only Settable via Windows Software
124 | Fuel Trip Delay | Monitoring time of fuel level after which fuel level trip is generated. | 10 Sec | 1-999 Sec | 10 Sec |  | Only Settable via Windows Software
125 | LLOP Trip Level | Monitoring value of lube oil pressure below which LLOP trip is generated. | 0.7 Kg/Cm2 | 0.3-8.5 Kg/cm2 Disable | 1.6 Kg/Cm2 |  | Only Settable via Windows Software
126 | LLOP Trip Delay | Monitoring time of lube oil pressure after which LLOP trip is generated. | 10 Sec | 0-999 Sec | 10 Sec |  | Only Settable via Windows Software
127 | HET Trip Level | Monitoring value of water temperature above which HET trip is generated. | Disabled | 40-251 Disabled* | 110C | Same setting for either HET/HWT | Only Settable via Windows Software
128 | HET Trip Delay | Monitoring time of water temperature after which HET trip is generated. | 10 Sec | 10-60 Sec | 10 Sec | Same setting for either HET/HWT | Only Settable via Windows Software
129 | Digital Input 1 Delay | Delay for programmable digital input. Digital input are explained above. | 10 Sec | 1-99 Sec | 5 Sec |  | Settable via Keypad on Controller or Windows Software
130 | Digital Input 2 Delay | Delay for programmable digital input. Digital input are explained above. | 10 Sec | 1-99 Sec | 5 Sec |  | Settable via Keypad on Controller or Windows Software
131 | Digital Input 3 Delay | Delay for programmable digital input. Digital input are explained above. | 10 Sec | 1-99 Sec | 5 Sec |  | Only Settable via Windows Software
132 | Digital Input 4 Delay | Delay for programmable digital input. Digital input are explained above. | 10 Sec | 1-99 Sec | 5 Sec |  | Settable via Keypad on Controller or Windows Software
133 | Digital Input 5 Delay | Delay for programmable digital input. Digital input are explained above. | 10 Sec | 1-99 Sec | 5 Sec |  | Settable via Keypad on Controller or Windows Software
134 | Digital Input 6 Delay | Delay for programmable digital input. Digital input are explained above. | 10 Sec | 1-99 Sec | 10 Sec |  | Settable via Keypad on Controller or Windows Software
135 | Digital Input 7 Delay | Delay for programmable digital input. Digital input are explained above. | 10 Sec | 1-99 Sec | 10 Sec |  | Only Settable via Windows Software
136 | Digital Input 8 Delay | Delay for programmable digital input. Digital input are explained above. | 10 Sec | 1-99 Sec | 10 Sec |  | Settable via Keypad on Controller or Windows Software
137 | Chg Alt-V Belt Delay | Duration for which the V-Belt signal should be continuously deactive to be recognized as a fault and action initiated. This fault is only enabled while the generator is running. | 180 Sec | Disable* 1-299 Sec | Disable |  | Settable via Keypad on Controller or Windows Software
138 | Hooter ON Time | Duration for which the hooter shall be ON, if not externally reset, while announcing a fault. | 30 Sec | 1-299 Sec | 299 Sec |  | Settable via Keypad on Controller or Windows Software
139 | Crank ON Time | Maximum crank time | 2.0 Sec | 0.5-20 Sec | 3.0 Sec |  | Settable via Keypad on Controller or Windows Software
140 | Crank Gap Time | The delay between two successive cranks | 10 Sec | 1-99 Sec | 5 Sec |  | Settable via Keypad on Controller or Windows Software
141 | Crank Attempts | The maximum number of cranks that shall be issued to start the Engine | 3 | 3-5 | 3 |  | Settable via Keypad on Controller or Windows Software
142 | Solenoid ON time | The time for which stop solenoid will be kept active while stopping the engine | 35 Sec | 1-99 Sec | 30 Sec |  | Settable via Keypad on Controller or Windows Software
143 | Disp Auto Scroll | Setting ON will enable Auto Scroll of display. OFF: No scroll and next parameter can be viewed by pressing next switch | ON | ON/OFF | ON |  | Settable via Keypad on Controller or Windows Software
144 | Scrolling Delay | After this duration next parameter Displayed on Display. | 10 Sec | 5-99Sec | 10 Sec |  | Settable via Keypad on Controller or Windows Software
145 | Battery UV Warning | Min. permissible battery voltage, below this the voltage is treated unhealthy & warning is generated. | 10.0 V | Disabled* 7.9-12V | 8.5 V |  | Settable via Keypad on Controller or Windows Software
146 | Battery OV Warning | Max. permissible battery voltage, above this the voltage is treated unhealthy & warning is generated. | 14.5 V | 12-30V Disabled* | 16V |  | Settable via Keypad on Controller or Windows Software
147 | Canopy Over Temp. | Monitoring value of Canopy Temp. Above which Canopy temp. Is generated. | 27.0 Celsius | 15.0-99.9 Celsius | 70.0 Celsius |  | Settable via Keypad on Controller or Windows Software
148 | Canopy Over Temp. Delay | Monitoring Time value of Canopy Temp. After which Canopy temp. Is generated. | 20 sec | 1-999Sec | 20 sec |  | Settable via Keypad on Controller or Windows Software
149 | NCD Strategy | Enable or Disable NCD (NOx Control Diagnostic) System as per CPCB4+ guidelines | Disabled* | Disabled* Enabled | Enabled |  | Settable via Keypad on Controller or Windows Software
150 | NCD Warn Hrs | Set the time in Hrs while Generator is running after which NCD Warning will get activated if any EGR warning remains in the system during this whole period. | 36.00 Hrs | 0.01-99.99 Hrs | 36.00 Hrs |  | Settable via Keypad on Controller or Windows Software
151 | NCD Fault Hrs | Set the time in Hrs while Generator is running after which NCD Fault will get activated if any EGR warning remains in the system during this whole period. | 72.00 Hrs | 0.01-99.99 Hrs | 72.00 Hrs |  | Settable via Keypad on Controller or Windows Software
152 | NCD Heal Hrs | Set the time in Hrs while Generator is running after which NCD Error timer will get reset if no EGR warning remains in the system during this whole period. | 40.00 Hrs | 0.01-99.99 Hrs | 40.00 Hrs |  | Settable via Keypad on Controller or Windows Software
153 | Ann. DG On | Selected contact is activated if Generator is on | No Annuciation | Disabled Contact on pin 1-12 | No Annunciation |  | Settable via Keypad on Controller or Windows Software
154 | Ann. DG Off | Selected contact is activated if Generator is off. | No Annuciation | Disabled Contact on pin 1-12 | No Annunciation |  | Settable via Keypad on Controller or Windows Software
155 | Ann. DG On Load | Selected contact is activated if Generator is On load | On Contact 7 | Disabled Contact on pin 1-12 | On Contact 10 |  | Settable via Keypad on Controller or Windows Software
156 | Ann. Unit OK | Selected contact is activated if unit is ok. | No Annuciation | Disabled Contact on pin 1-12 | No Annunciation |  | Settable via Keypad on Controller or Windows Software
157 | Ann. Fuel Trip | Selected contact is activated if fuel fault registered | On Contact 10 | Disabled Contact on pin 1-12 | On Contact 9 |  | Settable via Keypad on Controller or Windows Software
158 | Ann. LLOP Trip | Selected contact is activated if LLOP fault registered | On Contact 1 | Disabled Contact on pin 1-12 | On Contact 1 |  | Settable via Keypad on Controller or Windows Software
159 | Ann. HET Trip | Selected contact is activated if HET fault registered. | On Contact 2 | Disabled Contact on pin 1-12 | On Contact 2 | Same setting for HET/HWT | Settable via Keypad on Controller or Windows Software
160 | Ann. DG Voltage | Selected contact is activated if Generator voltage is healthy. | No Annuciation | Disabled Contact on pin 1-12 | No Annunciation |  | Settable via Keypad on Controller or Windows Software
161 | Ann. Emergency | Selected contact is activated if emergency fault is registered. | No Annuciation | Disabled Contact on pin 1-12 | No Annunciation |  | Settable via Keypad on Controller or Windows Software
162 | Ann. DG Overload | Selected contact is activated if generator is overloaded. | On Contact 3 | Disabled Contact on pin 1-12 | On Contact 3 |  | Settable via Keypad on Controller or Windows Software
163 | Ann. DG High Load | Selected contact is activated if generator is highloaded. | No Annuciation | Disabled Contact on pin 1-12 | No Annunciation |  | Settable via Keypad on Controller or Windows Software
164 | Ann. DG Frequency | Selected contact is activated if generator over frequency/under frequency fault registered | On Contact 5 | Disabled Contact on pin 1-12 | No Annunciation |  | Settable via Keypad on Controller or Windows Software
165 | Ann. RWL Fault | Selected contact is activated if RWL fault registered. | On Contact 8 | Disabled Contact on pin 1-12 | No Annunciation |  | Settable via Keypad on Controller or Windows Software
166 | Ann. Charging alternator/ V-belt | Selected contact is activated if Charging alternator/V-belt fault registered. | On Contact 6 | Disabled Contact on pin 1-12 | No Annunciation |  | Settable via Keypad on Controller or Windows Software
167 | Ann. Fail to Start | Selected contact is activated if Fail to Start fault registered. | On Contact 11 | Disabled Contact on pin 1-12 | On Contact 5 |  | Settable via Keypad on Controller or Windows Software
168 | Ann. Fail to stop | Selected contact is activated if Fail to stop fault registered. | On Contact 12 | Disabled Contact on pin 1-12 | On Contact 6 |  | Settable via Keypad on Controller or Windows Software
169 | Ann. Current Unbalance | Selected contact is activated if Current Unbalance fault registered. | No Annunciation | Disabled Contact on pin 1-12 | No Annunciation |  | Settable via Keypad on Controller or Windows Software
170 | Ann. Fuel Open | Selected contact is activated if fuel sensor is open. | No Annunciation | Disabled Contact on pin 1-12 | No Annunciation |  | Settable via Keypad on Controller or Windows Software
171 | Ann. LLOP Open | Selected contact is activated if LLOP sensor is open. | No Annunciation | Disabled Contact on pin 1-12 | No Annunciation |  | Settable via Keypad on Controller or Windows Software
172 | Ann. HET Open | Selected contact is activated if HET sensor is open. | No Annunciation | Disabled Contact on pin 1-12 | No Annunciation |  | Settable via Keypad on Controller or Windows Software
173 | Ann. Canopy Temperature | Selected contact is activated if Canopy Temperature is high. | No Annunciation | Disabled Contact on pin 1-12 | On Contact 7 |  | Settable via Keypad on Controller or Windows Software
174 | Ann. Fire | Selected contact is activated if ﬁre fault registered. | No Annunciation | Disabled Contact on pin 1-12 | No Annunciation |  | Settable via Keypad on Controller or Windows Software
175 | Ann. Oil Temperature | Selected contact is activated if Oil Temperature is high | No Annunciation | Disabled Contact on pin 1-12 | No Annunciation |  | Settable via Keypad on Controller or Windows Software
176 | Ann. Oil level | Selected contact is activated if Oil level is low. | No Annunciation | Disabled Contact on pin 1-12 | No Annunciation |  | Settable via Keypad on Controller or Windows Software
177 | Ann. Service Due | Selected contact is activated if Service is due. | No Annunciation | Disabled Contact on pin 1-12 | No Annunciation |  | Settable via Keypad on Controller or Windows Software
178 | Ann. Battery NOK | Selected contact is activated if battery voltage is unhealthy | No Annunciation | Disabled Contact on pin 1-12 | No Annunciation |  | Settable via Keypad on Controller or Windows Software
179 | Ann. common Fault | Selected contact is activated if generator stopped on any fault | On Contact 4 | Disabled Contact on pin 1-12 | On Contact 4 |  | Settable via Keypad on Controller or Windows Software
180 | Ann. Half Fuel Warning | Selected contact is activated if low fuel warning is generated | On Contact 9 | Disabled Contact on pin 1-12 | No Annunciation |  | Settable via Keypad on Controller or Windows Software
181 | Ann. C Door Open | Selected contact is activated if Canopy Door is opened | No Annunciation | Disabled Contact on pin 1-12 | No Annunciation |  | Settable via Keypad on Controller or Windows Software
182 | Ann. Gen. Rev. power | Selected contact is activated if Gen. Rev. power fault is generated | No Annunciation | Disabled Contact on pin 1-12 | No Annunciation |  | Settable via Keypad on Controller or Windows Software
183 | Ann. EGR Warn | Selected contact is activated if any EGR Warning is active | No Annunciation | Disabled Contact on pin 1-12 | No Annunciation |  | Settable via Keypad on Controller or Windows Software
184 | Ann. NCD Warn | Selected contact is activated if NCD Warning is active | No Annunciation | Disabled Contact on pin 1-12 | No Annunciation |  | Settable via Keypad on Controller or Windows Software
185 | Ann. NCD Fault | Selected contact is activated if NCD Fault is active | No Annunciation | Disabled Contact on pin 1-12 | On Contact 11 |  | Settable via Keypad on Controller or Windows Software
186 | Ann. CPCB4+ Audio | Selected contact is activated according to CPCB4+ Audio indication requirements (Active every 5 seconds for 2 seconds when NCD Warning active and Active every 2 seconds for 2 seconds when NCD Fault is acive other wise not active) | No Annunciation | Disabled Contact on pin 1-12 | On Contact 12 |  | Settable via Keypad on Controller or Windows Software
187 | Device Id | Mod bus device ID | 1 | 1-247 | 1 |  | Settable via Keypad on Controller or Windows Software
188 | Baud Rate | RS 485 Communication Baud rate | 9600 | 1200 2400 4800 9600 19200 | 9600 |  | Settable via Keypad on Controller or Windows Software
189 | Parity | RS 485 Communication Parity Bits | None | Even Odd None | None |  | Settable via Keypad on Controller or Windows Software
190 | Stop Bit | RS 485 Communication Stop Bits | 1 | 1 2 | 1 |  | Settable via Keypad on Controller or Windows Software