## Test Report
SEDEMAC |  | Test Report For : SW-GC2X-GC2115-RA6M2 | [8 empty] | Doc # | SW-TESTREPORT-GC2X-GC2115-RA6M2
[11 empty] | Rev #/ Rev Date | 0.27/21 June 2024
[11 empty] | Page # | 1 of 24
Test set up details
HW used (Board no / Part number etc) |  |  | SM0015046 R00, SM0015046 R1.0
Base code part no. With revision and version |  |  | SW_EXECUTABLE_GC2115_RA6M2 R0V27
GUI Part no. With revision and version |  |  | GCU Flasher R4.2.1.0
Boot Loader Part no. With revision and version |  |  | BL_RA6M2_GC2K_V1.16_CONTRAST80_PLM13199
Configuration files used |  |  | CFGZ 2115
Test Rig Part no. With revision and version |  |  | SW-GC2X-TR02, SW-GC2X-TR01 (R2.0)
Test Rig Code Part no. With revision and Version |  |  | NA
Other relevant information |  |  | NA
Source code details of software subjected to test: |  | BitBucket Project: | SW-GC2X
|  | Repository: | gc2111_renesas
|  | Branch: | gc2115_renesas_mnm
|  | Commit ID: | 36c97b6
Tag:
"Test Cases" document details: |  |  | SW-TESTCASES-EXECUTABLE-GC211X-RA6M2 | [6 empty] | "Test Cases" Document Rev # & Rev Date
Sr. No. | Test Case ID | Description | Module/ Functionality under test | Corresponding SRS ID | Expected result | Actual result Firmware R0V07 | Actual result Firmware R0V23 | Actual result Firmware R0V25 | Actual result Firmware R0V27 | Pass/Fail | Tested by | Date of testing
1 | GCU_01 | Start up screen
|  | After flashing through GCU flashar Power on GCU and observe the screen | First time power on | FR 28 | After power on , GCU should display No_Profile_Selected Please go in CONFIG mode and select PROFILE | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-04
|  | Without selecting profile give power rest to the controller , power on device and go to config by master and user pin in CFGC |  |  | After entering CONFIG mode GCU should enter into write mode by master and user pin entered in CFGC | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-04
|  | Support of 10 profiles and Selection of profile with word "Master Password" PIN1 detailed test cases for profile selection enlisted test case GCU_49 |  | FR 28 | Support of 10 profiles and Selection of profile with word "Master Password" PIN1 detailed test cases for profile selection enlisted test case GCU_49 | Working as expected | Not tested in this build | Not tested in this build | As Expected | Pass | Rahul Hage | 2024-06-24
|  | Power on the GCU and observe the start up screen. | Start Up screen | FR 1 | After power on, GCU should display the home screen with the current mode and engine status screen. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-04
2 | GCU_02 | Engine Status screen
|  | Power on the GCU and observe the engine status screen. | Engine Status screen | FR 1 | After power on, GCU should display the engine status screen with the mode and the engine status. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-04
|  | After power on, simulate the shut down, electrical trip and warning alarms one by one and check the engine status screen. |  | FR 1 | When there is any alarm present, engine status screen should display the “Notification”, “Shut down” or “Warning” depending on the alarm present. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-04
|  | Set maximum cranking attempts and give start to GCU by start key (Manual) or make mains (Auto) | No. of cranking attempts display |  | GCU should display the current cranking attempt /maximum starting attempts correctly on Engine status screen when GCU gets start command | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-04
Product info screen
|  | After power on, check product info screen |  |  | GCU should display 1.version and revision of product 2. current Date and time correctly | Not tested in this build | Not tested in this build | Same as expected | Not tested in this build | Pass | Sangeet Wankhede | 2024-06-20
3 | GCU_03 | Electrical measurements of the L-L and L-N voltages are measured on the actual DG. Load bank is connected to the DG and Load is increased in steps. Actual phase voltages and currents are measured with the DMM and clamp meter, and the values are compared with the GCU readings.
|  | a) Apply the load on the DG and increase the Load on the DG step by step from 1KW to 10KW. Measure the value of the current for the each value of the load. Measure the L-N and L-L voltages and current in the each phase. | VI Measurements |  | GCU values should be equal to the DMM values. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | PASS | Upendra K | 2024-03-04
|  | b) Measure the values of the voltages and current for the 3PH and 1PH configurations. |  |  | GCU should display the phase voltages and currents accurately for both 1PH as well as 3PH configurations.
|  | c) Keep mains monitoring ON. Keep under voltage monitoring disabled and under frequency monitoring enable and disconnect mains any 1 phase |  |  | GCU should show mains unhealthy | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | PASS | Purushottam P | 2024-03-06
|  | d) Keep mains monitoring ON. Disconnect any one phase by keeping under voltage and under frequency monitoring enable |  |  | GCU should show mains unhealthy | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | PASS | Purushottam P | 2024-03-06
|  | e) Keep mains monitoring enable. Reduce phase voltages such that any one of the line to line voltage goes below under volt threshold |  |  | GCU should show mains unhealthy | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | PASS | Purushottam P | 2024-03-06
4 | GCU_04 | SMD Start/Stop and contactor handling In the manual mode. | SMD Start/Stop
|  | Configure the power on mode as Manual. Keep the mains monitoring disabled and then power reset the GCU. | Mains Monitoring Disabled in the manual mode. |  | When the mains monitoring is disabled, then after power on, mains contactor should not get latched and DG contactor should be open.
|  | Configure the power on mode as Manual. Keep the mains monitoring enabled and then power reset the GCU. | Mains Monitoring Enabled. |  | When the mains monitoring is enabled, then the GCU should monitor the mains first and then it should close the mains contactor if the mains is detected as healthy and mains contactor latch key is pressed.
|  | Enable the auto load transfer and press the start key when the GCU is in the manual mode. | Start with Auto Load transfer Enabled |  | With no error present, DG should start after the set start delay. DG contactor should be closed when the generator voltage and frequency are above the healthy threshold.
|  | Disable the auto load transfer and then press the start key. | Start with Auto Load transfer Disabled |  | With no error present, DG should start. DG contactor should not be closed as the auto load transfer is disabled.
|  | Set the number of crank attempts. Set the crank time and crank rest time. Disconnect the start relay output. Press the start button. | To Start Alarm |  | DG should give the crank attempts for the set number of times. Cranking output should be high for the crank time and it should be off for the crank rest time. After the cranking attempts, GCU should give the to start alarm.
|  | Keep the auto load transfer disabled and then Start the DG. Make the mains healthy or unhealthy when the DG is running. | Mains Monitoring while the engine is ON |  | When the DG is running, then also GCU should detect the mains and it should close or open the mains contactor according to mains contactor latching key press.
|  | Press start when error is present. | Start command when alarm is present |  | DG should not start and mains contactor should remain in the same state.
|  | Press the Stop key in the Crank Start delay. |  |  | DG should stop the starting sequence.
|  | Press stop in the middle of the first cranking. |  |  | DG should stop.
|  | Press stop in the crank rest time. |  |  | DG should stop.
|  | Press stop during the subsequent cranking. |  |  | DG should stop.
|  | Press start when the maintenance due alarm is active. |  |  | DG should start and DG contactor should get closed when the DG turns ON if the auto load transfer is ON. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-05
|  | Press the start (give the crank output) during running. |  |  | DG should not give the start command and it should keep running as it is and load should be ON DG.
|  | Press start during stopping sequence. |  |  | DG should not give the cranking output during stopping sequence.
|  | Press stop once. |  |  | DG Should stop after the cooling down time when the stop is pressed once. Mains contactor should be closed if we press the Mains latching key and DG contactor should be opened as soon as the STOP is pressed.
|  | Press stop key twice(immediately after one another). |  |  | DG should stop immediately.
|  | Simulate the to stop situation by disconnecting the Stop relay. |  |  | GCU should start the stop action time when the stop is pressed and should give the to stop alarm when the stop action time is over. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-05
|  | Disconnect the DG output from the GCU and then give start command. And then connect the DG output in during the crank rest time. |  |  | Engine start should be detected during the Crank rest time also and GCU should not give the next cranking pulse. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-05
|  | Keep the DG off. Press the auto button to keep the DG in Auto mode. Press Auto again. |  |  | GCU should go to the auto mode when the auto is pressed and should return to the manual mode if the auto is pressed again.
|  | Start the DG manually. Press the auto key when the DG is running. |  |  | When the auto key is pressed during engine ON state, then the GCU should switch to the auto mode.
|  | Start the DG manually and simulate any fault condition. When the DG stops due to an alarm, make the mains healthy and unhealthy several times. |  |  | When the DG is stopped due to an alarm, then GCU should detect the mains and it should close or open the mains contactor according to the status of the mains and mains contactor latching key status.
|  | Test to be performed on the DG. Keep the stop hold delay less than 5 seconds. Start the DG and then press the stop key during cranking sequence itself. |  |  | DG should stop completely when the stop key is pressed during the cranking sequence. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-05
|  | Power reset the GCU when the engine is already running or start the engine externally(without pressing the start key). | Illegal Engine On(Alternator Wave detection disabled) | FR 7 | When the engine is started externally, then the GCU should accept this engine On and should allow the DG to run, Number of starts should be increased by 1.
5 | GCU_05 | SMD AMF
|  | Enter the configuration mode of the GCU and enable the mains monitoring. Select one of the outputs as “Close DG contactor” and other as “Close Mains contactor”. Connect the lamps to these outputs and observe the status of those outputs. Connect the mains supply to the mains input and then follow the below procedure and observe the behaviour of the GCU. - Behaviour of the GCU will be the same in KEYPAD and Input as a mode selector switch mode. |  | FR 1
|  | - Put the GCU in the auto mode when the mains is healthy first. Also repeat the same when the mains is unhealthy. |  |  | After entering the auto mode, GCU should take the mains detect delay first. After the mains detect delay, GCU should take the action as per the mains status. When the mains is detected as healthy, Genset should remain off and load should remain on the mains. If the Genset is starting, then GCU should take the start delay.
|  | Make the mains unhealthy when the Genset is in the auto mode. |  |  | GCU should take the mains detect delay first. And when the mains is detected as unhealthy after the mains detect delay, it should give the start command after start delay.
|  | Press the stop key and put the GCU in the manual mode. Make the mains unhealthy when the GCU is in the manual mode and then press the auto key to put the GCU in the auto mode. |  |  | After entering in the auto mode, GCU should not give the start command immediately. Instead, it should take the mains detect delay first an then it should take the action as per the mains status.
|  | Allow the Genset to start in the auto mode by cutting the mains off. Make the mains healthy when the Genset is running. |  |  | GCU should take the mains detect delay first. Then it should take the return to mains delay and then the load should be switched on the mains. Genset should stop after the cooling down time.
|  | Simulate any shut down alarm when the Genset is running with the load. |  |  | Genset should stop immediately when the shut down occurs.
|  | Simulate any electrical trip alarm when the Genset is running with the load. |  |  | Genset contactor should get opened and engine should stop after cooling down time when the electrical trip occurs
|  | When the Genset is stopped due to alarm, turn on the mains supply and make mains healthy. |  |  | When the Genset is in the fault mode and mains returns, then the mains contactor should get latched after the mains detect delay.
|  | Turn off the mains supply when the cooling down timer is running. condition:- mains detect delay should be less than cooling down time |  |  | When the mains becomes unhealthy during cooling down time, then the GCU should not close the mains contactor after mains detect delay and Genset should keep running with load. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-05
|  | Allow the Genset to start in the auto mode and then press the auto key. |  |  | When the auto key is pressed in the auto mode while engine is running, GCU should switch the mode. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-05
|  | Enable the auto load transfer, Start the Genset manually and then press the auto key. Keep the mains unhealthy. |  |  | Genset should keep running with the load as it is when auto is pressed. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-05
|  | Start the Genset manually and then press the auto by keeping the mains healthy. |  |  | When the Genset is running, GCU should switch the mode from manual to auto even the auto key is pressed and GCU should takes mains detect delay detects mains helathy, by taking return to mains delay and DG should DG stops followed by cooling down time and Mains contactor gets latched. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-05
|  | Simulate the FAIL to stop situation and then cut off the mains. |  |  | When the FAIL to stop alarm occurs, then also the GCU should monitor the mains and it should close or open the mains contactor according to the mains status. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-05
|  | Disconnect the Genset input connector from the GCU. Cut off the mains and during crank rest time, connect the Genset connector to the GCU again. |  |  | GCU should detect the Genset ON in the crank rest time also and it should not give the next crank.
|  | Press start key when the Genset is in the auto mode. |  |  | Genset should ignore start.
|  | Press the stop key when the Genset is in the auto mode. |  |  | Genset should come out of the auto mode if it is not running. If the Genset is running, then it should take stop in manual mode by taking the cooling down time. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-05
|  | Simulate any alarm condition in the auto mode. Then clear the electric trip or shutdown alarm alarm by pressing the ack key. |  |  | If the trip or shutdown alarm occurs in the auto mode and if the alarm is cleared in the auto mode, then GCU should not switch the mode of the GCU & should take the action as per the mains status. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-05
|  | Make the mains unhealthy. Allow the GCU to give the start command and make the mains healthy when the start delay timer is running. Condition:- start delay should be greater than mains detect delay |  |  | When the mains is detected as healthy during start delay, then GCU should stop the starting sequence and should stop immediately without taking any delay . | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-05
|  | Make the mains healthy when the cranking attempt is going on. Condition:- crank start delay should be greater than mains detect delay |  |  | When the mains is detected as healthy during cranking sequence, then GCU should stop the cranking and Genset should stop. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-05
|  | Make the mains unhealthy in the auto mode. | DG contactor in the Auto mode |  | When the mains becomes unhealthy, then GCU should issue the start command. When the engine starts, GCU should start the warm up delay & Genset becomes healthy when warm up delay is over. Genset contactor should get latched after the load transfer delay is over.
|  | Make the mains unhealthy in the auto mode and make it healthy again before the warm up delay is over. Condition:-wram up delay should be greater than mains detect delay |  |  | If the mains is detected as healthy before the warm up delay is over, then the GCU should issue the stop command immediately without taking the cooling down time. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-05
|  | Allow the Genset to start in the auto mode by cutting off the mains. After the warm up delay is over, GCU will start the load transfer delay. Simulate the electrical trip alarm in the transfer delay. Condition:-load transfer delay should be greater than warm up delay. |  |  | If the electrical trip is generated during the transfer delay, then the GCU should take the cooling down time and then it should issue the stop command. In this case GCU should not latch the Genset contactor once the electrical trip is generated. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-05
|  | Use Mode selector switch a input & give input when mains is unhealthy. Also repeat same when mains is healthy. | Input mode selector As Input as a mode selector switch | FR 8 | After giving input GCU should enter in the auto mode, GCU should behave same as in above Auto mode when input is selected. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-05
|  | Set power ON mode as Manual. Power ON GCU, give mode selector input & Simulate MAINS , while auto start delay time remove input. |  |  | In auto start delay time if mode is changed to manual by mode selector switch input, GCU mode should change to Manual mode and start command should continue with manual start delay timer. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-05
|  | Change mode in Preheat time |  |  | In preheat timer if mode is changed to manual by mode selector switch input, GCU mode should change to Manual and start command should continue with previous (auto mode) preheat timer.(preheat timer should not restart) | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-05
|  | Change mode in Crank time |  |  | In crank timer if mode is changed to manual by mode selector switch input, GCU mode should change to Manual and start command should continue with previous (auto mode) crank timer.
|  | Change mode in safety monitoring delay |  |  | In safety monitoring delay time if mode is changed to manual by mode selector switch input, GCU mode should changed to Manual and Genset should be running continues with previous (auto mode) safety monitoring delay timer.
|  | Change mode after Genset contactor get latched |  |  | If Auto load transfer is disabled & mode is changed to manual by mode selector switch input after Genset contactor latched, GCU mode should changed to Manual and Genset should be running continues and Genset contactor should get unlatch. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-05
|  | Change mode in alarm condition, |  |  | If mode is changed to manual by mode selector switch input. Simulate any alarm, GCU mode should changed to Manual and Alarm should be reset. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-05
|  | Change mode in cooling time |  |  | If mode is changed to manual by mode selector switch input while cooling time, GCU mode should changed to Manual and cooling time should continue in manual mode | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-05
6 | GCU_06 | SMD Remote Start/Stop
Configure one of the inputs as Remote start/stop and set the activation delay for the same. GCU will enter the remote start stop mode only when the mains monitoring is disabled. When the input is activated, GCU will receive the start command and when the input is de-activated, GCU will receive the stop command. Note :- do not configure mode selecter switch, BTS monitoring Disabled, Cyclic mode disable, Night mode disable
|  | a) Put the GCU in the auto mode and keep the remote start/stop input de-active. | Remote Stop Command. | FR 1 | When the remote start input is not active, Genset should remain off. GCU should treat the remote stop command same as “Mains Healthy” condition and mains contactor should remain latched in this case.
|  | b) Put the CGU in the auto mode first and then activate the Remote start input and keep that input latched to the active state. | Remote start Command | FR 1 | When the remote start is activated and is latched for the activation delay of that input, GCU should issue the start command to the Genset. Genset should keep running as long as the input is active.
|  | c) Allow the Genset to start in the auto mode by remote start command and observe the Genset contactor. | DG contactor in Remote start/stop mode | FR 1 | When the Genset is ON due to the remote start, then GCU should wait till the Genset is healthy. After the Genset becomes healthy, GCU should start the warm up delay. After the warm up delay is over load transfer delay starts & GCU should latch the Genset contactor after transfer delay. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-05
|  | d) Simulate any warning alarm during the warm up delay and clear it before the warm up delay is over. | Warning alarm in the warm up delay |  | If any warning occured during the warm up delay, then GCU should take shutdown action and GCU should stop. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-05
Note: In the Remote start/Stop mode, GCU should behave same as AMF. For GCU, Remote start is equivalent to mains unhealthy and Remote stop is equivalent to mains healthy. do not configure Mode selector switch
7 | GCU_07 | Test Mode
|  | Power on mode as manual mode. Press auto key for 3 sec. |  |  | GCU should change mode to Test mode with auto & start LED should blink continuously. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-05
|  | Press the Auto for the 3 seconds when GCU is in the AUTO mode. |  |  | GCU should not enter the TEST mode. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-05
|  | Press start when no error is present. | Start command when no alarm |  | Genset should take start with start delay displayed on status screen | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-05
|  | Set the test mode timer from the configuration menu and press the start key. | Test mode timer |  | After pressing the start key, GCU should start the DG and when the DG starts, start and auto LED should blink continuously and in the test mode, GCU should not close the generator contactor. DG should keep running for the set time in the test mode timer and when this timer expires, DG should stop and GCU should enter into the manual mode. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-05
|  | Start the DG in the TEST mode and then turn ON and OFF the mains supply and observe the mains contactor status | Mains monitoring the TEST mode. |  | When the DG is running in the test mode, then the GCU should monitor the mains.Mains contactor should get latched if it present even Test mode is ON & engine is running, if Mains is failed then mains contactor should get unlatched & if mains restored the mains contactor should not get latched again. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-05
8 | GCU_08 | BTS Battery monitoring.
|  | Enable Mains monitoring, Remote start, Cyclic mode, BTS monitoring and observe priority in Auto mode | Priority to BTS monitoring | FR 2 | When all these parameters are enabled then GCU should give first priority to BTS monitoring functionality | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-05
|  | Activate the BTS monitoring in auto mode. Keep mains healthy | Mains healthy in the BTS Monitoring enable | FR 2 | When the mains becomes healthy, GCU should take the mains detect delay first. If the mains remains healthy for the mains detect delay time, then only the GCU should declare the mains as healthy. Mains healthy or unhealthy condition is decided based on the trip and return values of the mains voltage and frequency. Mains contactor should get latch. GCU will show 'Auto-BTS battery backup' mode
|  | Make the mains unhealthy when the GCU is already in the auto mode, and Keep BTS voltage healthy | Mains unhealthy while BTS is healthy | FR 2 | When the mains becomes unhealthy, GCU should wait till the mains detect delay is over. Same time GCU will monitor BTS voltage is healthy or not, If BTS voltage is healthy then GCU will not give start command to DG. GCU will show 'Auto-BTS battery backup' mode. If the mains is detected as unhealthy for the time set in the mains detect delay, then GCU should open the mains contactor.
|  | Make the mains unhealthy when the GCU is already in the auto mode, and set BTS voltage unhealthy | Mains unhealthy while BTS is unhealthy | FR 2 | When the mains becomes unhealthy, GCU should wait till the mains detect delay is over. Same time GCU will monitor BTS voltage is healthy or not, If BTS voltage is healthy then GCU will not give start command to DG. GCU will show 'Auto-BTS battery backup' mode. If the mains is detected as unhealthy for the time set in the mains detect delay, then GCU should open the mains contactor and then it should issue the start command after start delay in auto mode. GCU should show 'DG run duration' which is setted
|  | Simulate any alarm condition when the DG is running in auto mode. When the DG is stopped due to an alarm, make the mains healthy and unhealthy several times. | Mains Monitoring when the alarm is pending. | FR 2 | When any alarm is pending and GCU is in the AMF mode, then GCU should monitor the mains and it should latch or unlatch the mains contactor according to the mains status. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-05
|  | Mains and BTS unhealthy in auto mode. When DG crank then make the BTS healthy and unhealthy several times. | BTS Monitoring when the DG crank | FR 2 | When DG cranks and GCU sense BTS healthy in the auto mode, then GCU should monitor the BTS and it should issue the stop command. If again BTS unhealthy sensed by GCU, It should again issue the start command with start delay time. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-05
|  | Simulate DG start in Auto-BTS battery backup mode | DG stop when DG run duration is over | FR 2 | Set DG Run duration time, simulate DG start in Auto- BTS battery Backup mode. GCU show remaining time on screen. After finishing DG run duration time, GCU should issue contactor unlatch as well as stop command with cooling time | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-05
|  | Simulate DG start in Auto-BTS battery backup mode, Keep BTS unhealthy | BTS unhealthy after completion of DG on timer. | FR 2 | Set DG Run duration time, simulate DG start in Auto- BTS battery Backup mode. GCU show remaining time on screen. After finishing DG run duration time, GCU should issue contactor unlatch as well as stop command with cooling time, due to BTS unhealthy GCU should repeat above cycle. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-05
|  | Allow the DG to start in the BTS mode by making the BTS low and Mains unhealthy. Simulate the BTS healthy condition during the Start delay or during warm up delay. | BTS healthy in the Start delay and Warm up delay. | FR 2 | GCU should issue the stop command.
|  | Allow the DG to start in the BTS mode by making the BTS low and Mains unhealthy. Simulate the mains healthy condition when the warm up delay is running. | Mains healthy during the warm up delay | FR 2 | When the mains healthy is detected in the warm up delay, GCU should stop DG without taking the cooling down time.
|  | Allow the DG to start in the due to BTS low. Allow the DG to run for few minutes. Make the BTS voltage healthy when the DG is running. | BTS healthy when the DG is running | FR 2 | If the BTS voltage is found healthy when the DG is running, then also DG should continue to run and should run for the DG on timer delay
|  | - Put the GCU in the auto mode by applying +Vcc (12VDC) to pin no 18, when the mains is healthy first. Also repeat the same when the mains is unhealthy.Select Polarity as Open to activate for DIG IN O > MODE select SWITCH | Input mode selector As Input as a mode selector switch.Select Polarity as Open to activate for DIG IN O > MODE select switch | FR 8 | After giving +Vcc GCU should enter in the auto mode, GCU should behave same as in above Auto mode when keypad input is selected | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-04-17
|  | Set power ON mode as Manual, after GCU power ON, connect +Vcc to pin 18, Simulate MAINS , while counting auto start delay time disconnect +Vcc |  |  | In auto start delay time if mode is changed to manual by Input as a mode selector switch input, GCU mode should turn on Manual and start command should continue with manual start delay timer. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-04-17
|  | Change mode in Preheat time |  |  | In preheat timer if mode is changed to manual by Input as a mode selector switch input, GCU mode should turn on Manual and start command should continue with previous (auto mode) preheat timer. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
|  | Change mode in Crank time |  |  | In crank timer if mode is changed to manual by Input as a mode selector switch input, GCU mode should turn on Manual and start command should continue with previous (auto mode) crank timer. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
|  | Change mode in safety monitoring delay |  |  | In safety monitoring delay time if mode is changed to manual by Input as a mode selector switch input, GCU mode should turn on Manual and DG should be running continues with previous (auto mode) safety monitoring delay timer. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
|  | Change mode after DG contactor get latched |  |  | If mode is changed to manual by Input as a mode selector switch input after DG contactor latched, GCU mode should turn on Manual and DG should be running continues and DG contactor should get unlatch. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
|  | Change mode in alarm condition, |  |  | If mode is changed to manual by Input as a mode selector switch input after simulate any alarm, GCU mode should turn to Manual and Alarm should be reset. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
|  | Change mode in cooling time |  |  | If mode is changed to manual by Input as a mode selector switch input while cooling time, GCU mode should turn to Manual and cooling time should continue in manual mode | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
9 | GCU_09 | SMD FOR SHELTER TEMPERATURE
|  | Keep the BTS monitoring ON.GCU should be in auto mode and Mains monitoring should be enabled. |  | FR 9
|  | a) keep Mains unhealthy BTS monitoring enabled. BTS voltage healthy and shelter temperature below High temp threshold value. Keep GCU in auto mode | BTS/site battery healthy, shelter Temperature healthy, mains unhealthy. |  | GCU should not start as all parameters are healthy and it should display AUTO-BTS BAT BACKUP on screen.
|  | b) keep the mains healthy. BTS monitoring on. BTS voltage unhealthy and shelter temperature unhealthy. Keep GCU in auto mode | Mains healthy and BTS battery, shelter Temperature healthy |  | As mains is healthy GCU should not issue the start command even if BTS and shelter temperature are unhealthy.
|  | c) keep the mains unhealthy. BTS monitoring on. BTS voltage unhealthy and shelter temperature healthy. | BTS/site battery unhealthy, shelter Temperature healthy, mains unhealthy. |  | As mains is unhealthy and BTS voltage is below threshold GCU should issue the start command and it should run for a set period of time for DG run duration for BTS. DG contactor should be latched for this duration. After finishing DG run duration time, GCU should unlatch the contactor as well as issue stop command with cooling time. And then take action as per the status of BTS voltage.
|  | d) keep the mains unhealthy. BTS monitoring on. BTS voltage healthy and shelter temperature above its threshold value. Set the shelter temperature monitoring delay, DG run duration. | BTS/site battery healthy, shelter Temperature unhealthy, mains unhealthy. |  | GCU should issue start command as mains is unhealthy and shelter temperature is above its threshold value. At the same time GCU should display high shelter temperature alarm. After finishing DG run duration time,GCU should issue contactor unlatch as well as stop command with cooling time. If Shelter temperature is still above its threshold GCU should repeat above cycle.
|  | e) Make mains unhealthy. Keep BTS battery voltage HEALTHY and shelter temperature unhealthy. Put GCU in auto mode. | BTS/site battery unhealthy, shelter Temperature unhealthy, mains unhealthy. |  | GCU should issue start command as mains is unhealthy BTS voltage and shelter temperature is unhealthy. At the same time GCU should display high shelter temperature alarm. DG should take BTS run duration.
|  | f) Make BTS battery voltage and shelter temperature unhealthy. Allow DG to start. Make mains healthy and unhealthy in between start delay and warm up delay. |  |  | Before the warm up delay if mains is healthy then GCU should issue stop command with shut down. After this GCU should takes the action as per the status of mains | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
|  | g) Make mains unhealthy. BTS battery voltage healthy and shelter temperature above its high threshold value. Allow DG to start due to shelter temperature. Make shelter temperature below high threshold but above low threshold when engine is ON. |  |  | GCU should issue the start command as shelter temperature is above its threshold value. If shelter temperature made healthy during engine on(Before safety Mon is over) GCU should not issue stop command and should recept the same cycle.
|  | g) Make mains unhealthy. BTS battery voltage healthy and shelter temperature above its high threshold value. Allow DG to start due to shelter temperature. Make shelter temperature healthy (Below low threshold ) when engine is ON after safety mon delay |  |  | GCU issue the start command as shelter temperature is above its threshold value. If shelter temperature made healthy during engine on (Below low threshold ) when engine is ON after safety mon delay then GCU issue stop command after completion of remianing min and DG stop by taking cool down time and takes the action as per mains and BTS
|  | g) Make mains unhealthy. BTS battery voltage unhealthy and shelter temperature below its high threshold value. Allow DG to start due to BTS battery. Make BTS battery voltage healthy when engine is ON. |  |  | GCU should issue the start command as BTS battery voltage is below its threshold and mains is unhealthy. Even if battery voltage made healthy during engine on(When GCU shows remaining min) GCU should not issue stop command and it should run for set duration of time.
|  | h) Make mains,shelter temperature unhealthy and BTS battery voltage healthy. Allow DG to start due to shelter temperature. During engine on Make BTS battery voltage unhealthy keeping shelter temperature above its threshold value. |  |  | After completing the DG run duration for shelter temperature GCU should not issue stop command and again it should repeat the same cycle | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-04-17
|  | i) Assign any digital input as mode select switch. allow DG to start due to shelter temperature. Change mode using switch to manual and again to auto mode. |  |  | Engine should run for set duration for Shelter temperature. After changing the mode from auto to manual and again from the manual to auto, then GCU should take the DG remaining time from the start. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-04-17
|  | j) Assign any digital input as mode select switch. allow DG to start due to BTS battery voltage unhealthy. Change mode using switch to manual and again to auto mode. |  |  | When the mode is changed from auto to manual GCU should enter the manual mode first. When the mode is changed again, then GCU should enter the auto mode and should take the DG run time from the start. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-04-17
10 | GCU_10 | Cyclic mode
Enable the cyclic mode and set the cyclic mode on timer and off timer. Put the GCU in the auto mode and follow the test cases as explained below.
|  | a) Put the GCU in the auto mode and observe the behaviour of the GCU. |  | FR 3 | After entering the auto mode, GCU should take the auto start delay first and then it should issue the start command. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
|  | Configuration: • Controller in Auto - Cyclic mode • Controller Idle mode Input: OFF • Mains healthy Action: • GCU power on in Auto mode • GCU transfer load on mains • Test person turn ON controller Idle mode • GCU update status as controller Idle mode • Test person turn OFF controller Idle mode |  |  | GCU should transfer load on mains when mains is detected as healthy For Controller Idle mode input ON GCU status Disaplay as Controller Idle Mode and GCU unlatch Mains contactor if mains is healthy |  | Idle mode i/p not available in input dropdown list
|  | Configuration: •Controller in Auto - Cyclic mode •Controller Idle mode Input: OFF •Mains monitoring Disable Action: •GCU start DG in Auto mode •GCU start DG in Auto cyclic for Genset ON time •After completing ON time GCU trigger stop action •Test person switch mode to manual mode •GCU continue cool down time •Test person switch mode to auto |  |  | •GCU should skip cool down timer and start DG •GCU should follow GCU ON - OFF timer in Auto - Cyclic mode |  | Idle mode i/p not available in input dropdown list
|  | Configuration: •Controller in Auto - Cyclic mode •Controller Idle mode Input: OFF •Mains monitoring Disable Action: •GCU start DG in Auto mode •GCU start DG in Auto cyclic for Genset ON time •Test person turn ON Controller Idle mode •GCU start cool down time •Test person switch mode to manual mode Result: •GCU update status as Manual Mode Engine on - healthy •GCU skip cool down time <<< Wrong •GCU keep DG running with load<<< Wrong •Stop LED continue blinking <<< Wrong |  |  | •GCU should continue cool down timer and stop DG |  | Idle mode i/p not available in input dropdown list
|  | b) Allow the DG to start in the cyclic mode. Observe the contactor status when the DG starts. |  | FR 3 | DG should start in the cyclic mode. After starting the DG, GCU should put the load on the DG by taking the warm up delay.
|  | c) Observe the monitoring screen when the DG is running in the cyclic mode. |  | FR 3 | When the DG is running in the cyclic mode, GCU should display the remaining time on the monitoring screen. GCU should start displaying the remaining minutes after completing the warm up delay. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
|  | d) Allow the DG to complete the DG on duration and then observe the behaviour of the GCU. |  | FR 3 | DG should run for the set duration of time. After this, DG should stop by taking the cooling down time.
|  | e) Check for the DG off timer. |  | FR 3 | When the DG stops after completing the DG on time, it should remain off for the set duration. Mains contactor should remain open when the DG is stopped.
|  | f) Simulate any fault condition when the DG is running in the cyclic mode. |  | FR 3 | When the alarm occurs in the cyclic mode, Then the GCU should stop the DG on timer.
|  | g) Put the GCU in the auto mode and observe the behaviour of the GCU. |  | FR 3 | After clearing the alarm, DG should start again and should start counting the DG on time from the beginning.
|  | h) Simulate the to start alarm when the DG is starting in the cyclic mode. |  | FR 3 | When the to start alarm occurs in the cyclic mode, then GCU should not start counting the DG on timer. After clearing the alarm, GCU should issue the start command again. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
|  | i) Press the stop key when the DG is running. When the DG stops completely, press the auto key again. |  | FR 3 | DG should stop when the stop key is pressed. GCU should enter the manual mode. After pressing the auto key, GCU should enter the cyclic mode and should issue the start command. DG should run for the set DG on timer.
|  | j)Enable the BTS mode and cyclic mode from the configuration. | Priority For the Cyclic mode | FR 3 | When the BTS mode and cyclic mode are enabled at the same time, then the GCU should run in the BTS mode only. GCU should run in the cyclic mode only when the BTS mode is disabled. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
|  | k) Enable the mains monitoring and cyclic mode at the same time. |  | FR 3 | In case, mains monitoring and cyclic mode are enabled at the same time, GCU should run in the cyclic mode only. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
|  | Enable the mains monitoring and cyclic mode at the same time mains healthy. |  |  | In case, mains monitoring and cyclic mode are enabled at the same time, GCU should run in the cyclic mode only and load should be on mains when mains is detected as healthy.
|  | l) Cyclic mode when Mains monitoring is disabled. Set DG on & Off time. Observe the behaviour of the GCU | Cyclic mode Mains Mon Disabled |  | In cyclic mode,if mains monitoring is disabled the it should start the DG for set ON time and it should be off according to set off time.
|  | m) Keep the mains monitoring disabled. Keep the Input as a mode selector switch on the auto position and power reset the GCU. | Power on mode and Input as a mode selector switch |  | After power reset, GCU should enter the auto mode. It should take mains detect delay and then should take the action accordingly. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
|  | n) Cyclic mode when Mains monitoring is enabled. Set DG on & Off time. Observe the behaviour of the GCU | Cyclic mode Mains Mon enabled |  | In cyclic mode,if main is monitoring is enabled then GCU should start the DG for set ON time and it should be off according to set off time according to mains condition | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
|  | o) Switch modes when cyclic mode is enabled | Mode Switching | FR 8 | When mode is switched, GCU should change the mode accordingly. It should reset the DG on timer every time Auto-Manual-auto mode change occurs. If mode is changed during DG off time GCU should start the DG on Timer
|  | p) Switch modes During Start delay | Mode switching during start Delay |  | Give start command in either auto or in manual mode. During start delay switch the mode. GCU should take the start delay according to the modes | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
|  | q) Change mode when alarm is pending | Mode switch during alarm |  | When mode is changed when alarm is present GCU should Clear the same alarms and switch the modes
|  | r) Alarm occurence in DG on mode | Alarm condition |  | If alarm is occurred during DG on time then GCU takes action accordingly. And after Shut down or electrical trip is cleared GCU starts DG on time again
|  | s) Simulate any alarm when the DG on timer is running and DG is running with the load. | Alarm condition |  | If the alarm is occurred in the DG on time, then GCU should take the action accordingly. After clearing the alarm, GCU should start the DG and should start the DG on time | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
|  | t) Make the mains healthy when the DG off timer is running and observe the behaviour of the GCU. | Mains healthy when the off timer is running. |  | If the mains is made healthy during off timer, then GCU should put the load on the mains and it should not display off timer on the screen. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
|  | u) Make the mains unhealthy after making it healthy in the off timer. |  |  | GCU should start the DG and should take the DG on time from the start. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
|  | v) Simulate the to start alarm in the above case. Or simulate any alarm during the warm up delay in the above case. Clear the alarm without making the mains healthy. | to start alarm after mains unhealthy in off timer. |  | GCU should start the DG and should start the ON timer. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
|  | w) Simulate any fault condition in DG ON time & Change mode in cooling delay. |  |  | GCU should take complete cooling delay & should stop properly. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
11 | GCU_11 | Load Measurement of Mains and DG in Manual mode
|  | Test to be performed on the RIG as well as on the DG. Select one of the inputs as a “Mains contactor latched” and another one as a “DG contactor latched”. Start the DG manually and apply the load on the DG. Keep the mains healthy. Keep the CT location as “On load Cable”. For testing on the DG, a appnel is used which can start/stop the engine externally. Also, it can apply the load on the mains and DG externally. | Feedback inputs enabled in the manual mode.
|  | Start the DG manually. Keep the mains healthy. Apply the load on the DG but do not activate any of the two feedback inputs. | Feedback inputs de-activated | FR 5, FR 6 | When both the feedback inputs are not active, then GCU should not display the current and load calculations for the mains and DG. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-06
|  | Simulate the DG on condition on the rig and then apply the load on it. Activate the DG contactor feed back input. | DG contactor latched | FR 5, FR 6 | GCU should measure the DG current and load only when the DG contactor latched input is active. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-06
|  | Start the DG externally. Disable the “Close Genset contactor output using DG contactor key. Apply the load on the DG externally and activate the “DG contactor latched” input. |  | FR 5, FR 6 | When the “Close DG contactor” output is not active and the “DG contactor latched” input is activated, then also GCU should start measuring the DG current and load. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-06
|  | Make the mains healthy. Put the load on the mains. Activate the :Mains contactor latched” input. | Mains contactor latched. | FR 5, FR 6 | GCU should start measuring the mains load and current only if the “Mains contactor latched” input is active. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-06
|  | Keep the mains healthy. Apply the load on the mains externally. Disable the “close mains contactor” output using the mains contactor key. |  | FR 5 | When the “Close mains contactor” output is not active and the “mains contactor latched” input is activated, then also GCU should start measuring the mains current and load. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-06
Disable the feedback inputs by entering the configuration menu. Keep the “Close mains contactor” and “Close DG contactor” outputs enabled in the configuration menu.
|  | Start the DG and when the DG becomes healthy, press the DG contactor key to apply the load on the DG. After this, make the mains healthy and then put the load on the mains using the mains contactor key. | Load measurement without feedback inputs | FR 5, FR 6 | When the feed back inputs are not configured, GCU should measure the load and current based on the contactor outputs for mains as well as DG. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-06
|  | Enter the configuration and disable the contactor outputs. Start the DG and apply the load on the DG manually. | Load measurement in case of MCP operation | FR 5 | When the contactor outputs and feedback inputs are not configured, then GCU should not latch contactor | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-06
12 | GCU_12 | Engine Status display Screen
While performing the test cases of SMD AMF and SMD start stop, observe the engine status screen during each sequence.
|  | Mode |  | FR 1 | GCU should display the mode of the DG in Normal font on the screen. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
|  | Ready |  | FR 1 | When there is no alarm and DG is ready to start, GCU should display the ready | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
|  | Starting |  | FR 1 | GCU should display the start delay with “Starting” string | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
|  | Crank hold: cranking |  | FR 1 | GCU should display the crank start delay when actual crank attempt is going on. During crank time period, GCU should turn off the back light. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
|  | Crank rest |  | FR 1 | GCU should display the crank rest time. Back light should be ON during the crank rest. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
|  | Running |  | FR 1 | When the DG is ON, GCU should display “Running” on the screen | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
|  | Alarm condition |  | FR 1 | When any alarm occurs, GCU should display “warning”, “Shut down” or “Notification” according to the alarm that is generated. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
|  | Preheating |  | FR 1 | GCU should display the preheat time when the preheating is going on. Back light should be turned ON during preheating. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
|  | Cooling down |  | FR 1 | GCU should display the cooling down time when the engine is cooling down | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
|  | Stopping |  | FR 1 | GCU should display the stopping time when the stop is pressed and GCU is stopping the DG. This should be displayed until DG stops or to stop alarm is generated. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
|  | Saving settings |  | FR 1 | GCU should display “saving settings” while coming out of the configuration mode. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
|  | Additional Stopping Delay |  | FR 1 | GCU should display stop hold timer until it expires. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
|  | Remaining minutes |  | FR 1 | GCU should display the remaining minutes of DG on time in case of BTS mode. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
13 | GCU_13 | Alarm acknowledgement
|  | Generate any fault condition to create the alarm or warning or notification and press alarm acknowledgement key to clear the alarm. | Alarm acknowledgement |  | When the alarm acknowledgement key is pressed, GCU should clear the alarm.
14 | GCU_14 | Sub-Menu Circular Caging
|  | a) In the GCU UI, select the configuration mode and check the sub menu of all the parameters be pressing up and down keys. | Sub Menu Circular Caging | FR 1 | GCU should display the sub menu parameters of the selected parameter only in circular manner. It should not go to the other parameter sub-menu. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
15 | GCU_15 | 1. Power On Mode
|  | a) Select the power on mode as an AUTO. Observe the behaviour of the GCU after power on, after coming out of the programming and after coming out of the Configuration mode. | Power On Mode as AUTO | FR 1 | GCU should go into the AUTO mode after coming out of the programming mode and after power on. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
|  | a) Select the power on mode as an Manual. Observe the behaviour of the GCU after power on, after coming out of the programming and after coming out of the Configuration mode. | Power On Mode as Manual | FR 1 | GCU should go into the Manual mode after coming out of the programming mode and after power on. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
2. Power On lamp Test.
|  | a) Enable the power on lamp test from the GCU or from the GUI. | Power On lamp Test. | FR 1 | All the LEDs should glow when the GCU is Powered On. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
16 | GCU_16 | 1.Display Contrast
|  | a) Set the contrast from the GUI or from the GCU and check whether the actual contrast changes according to the entered value. | Contrast | FR 1 | Contrast should change according to the value set by User and should give the proper display clarity when set at 50% | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
2. Power Save Mode
|  | 1. Enable the power save mode and set the power save mode delay in the timer section. 2. Check power save mode when Engine is ON | Power Save Mode | FR 1 | 1. The back light of the GCU should turn OFF after the power save mode delay is expired if the GCU is Idle. When the Power save mode is disabled, GCU should not turn off the back light. 2. GCU should not turn OFF backlight when Engine is Running and power save mode is Enable. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
17 | GCU_17 | ID and Numbers
|  | a) Set the Engine ID and profile ID from the GUI and check it in the GCU. |  | FR 1 | GCU should accept only the alphanumeric Engine ID and profile ID. GCU should accept only 12 Digit Engine ID and 20 digit profile ID with special character.Engine id should set from only GCU not from GUI | GUI not available
18 | GCU_18 | Communication
Select the communication mode as a MODBUS from the configuration menu. Check its functionality by connecting the RS485 cable to the GCU.
|  | a) Select the communication mode as a MODBUS. | MODBUS functionality | FR 4 | The parameters and registers should display the values and the bits as show in the MODBUS sheet. | Not tested in this build | Same as expected | Not tested in this build | Not tested in this build | Pass | Sangeet Wankhede | 2024-06-18
|  | b) Generate the alarms and check the register map for the alarms as per the table shown in the sheet 3. | Alarms | FR 4, FR22 | All the alarms should be displayed in the modbus poll as per the table. | Not tested in this build | Same as expected | Not tested in this build | Not tested in this build | Pass | Sangeet Wankhede | 2024-06-18
|  | c) Select any of the analogue input as Not used and then check the data on the MODBUS for that input. |  | FR 4 | GCU should send 0 on the MODBUS when any sensor is not used or used as a DIGITAL input. | Not tested in this build | Not tested in this build | Not tested in this build | Not tested in this build | NA | NA | NA
|  | d) Connect MODBUS and check MB count in event log display for 10 min |  | FR 21, FR 4 | GCU should increase MODBUS count after connection remains continuous for 10 min or during 10 Mins if communication is happened even once. GCU should monitor the status of connection for every 10 min.It should not increse MB count if GCU is power reset at any instant and should keep the modbus count same as per previous count | Not tested in this build | Not tested in this build | Not tested in this build | Not tested in this build | NA | NA | NA
|  | e) Check modbus poll error by selecting 115200 baud rate |  |  | Error should not come with change in baud rate | Not tested in this build | Same as expected | Not tested in this build | Not tested in this build | Pass | Sangeet Wankhede | 2024-06-18
|  | f) Fuel in percentage bit on modbus |  | FR 38 | Fuel in percentage should be display on modbus with scaling factor 1 | Not tested in this build | Same as expected | Not tested in this build | Not tested in this build | Pass | Sangeet Wankhede | 2024-06-18
19 | GCU_19 | Common mode implementation
|  | Pin number 16 on the GCU is used to read the EBP(Engine body potential). Connect the pot between the GCU ground and the analogue input. Then by applying the +2V or -2V to the EBP pin, check the LOP, Engine temp and the Fuel level for the different values of pot. |  | FR 1 | GCU should display the same readings when the voltage on the EBP pin is +2V, -2V and 0V with respect to the GCU ground.
|  | Connect the EBP pin to the ground and then take the readings for the LOP. Then apply the -2V on the EBP pin and then take the readings. Repeat the same procedure by applying the +2V to the EBP pin. | EBP Pin Voltage | FR 1 | GCU should display the same readings when the voltage on the EBP pin is +2V, -2V and 0V with respect to the GCU ground.
|  | Connect the EBP pin to the ground and then take the readings for the LOP and Fuel Volatge Sensor. Then apply the -2V on the EBP pin and then take the readings. Repeat the same procedure by applying the +2V to the EBP pin. |  |  | GCU should display the same readings when the voltage on the EBP pin is +2V, -2V and 0V with respect to the GCU ground.
20 | GCU_20 | Analogue Inputs
Test to be performed on the Rig. Pots are connected to the analogue inputs to simulate the change in the resistance and hence the change in the analogue quantity.
1. Engine Temperature
Disable The parameter of Engine Temp Bar from CFGC
|  | Set the high temperature warning and shutdown threshold. Simulate the high temperature warning and shutdown alarm using the pot. | Engine Temperature Action and threshold | FR 1 | GCU should generate the alarm and should take the action as per the configured high temp action when the temperature becomes higher than the threshold value.
|  | For different values of the resistances, check the temperature displayed by the GCU | Calibration table | FR 1 | GCU should display the values of the temperatures as per the configuration table for different values of the resistances.
|  | Enable the open circuit alarm for the temperature circuit. Disconnect the connector of the temperature input from the GCU to simulate the open circuit. | Temperature circuit open alarm | FR 1 | GCU should display the open circuit warning after 30s when the connector is disconnected from the GCU. When the open circuit alarm is disabled, GCU should not display warning.
2.Fuel Level Input
|  | Select the analogue input as a Fuel level input and enter the calibration table for the same. Set the Notification and shut down threshold for LFL. Simulate the Low fuel level by varying the pots connected to the analogue inputs. Fuel level sensor have monitaring Always. | Fuel Level Notification and Shut down | FR 49 | When the fuel level is below the notification threshold, GCU should gives the notification for the LFL. When the Fuel level becomes less than the shut down threshold, GCU should generates the shut down for the LFL.
|  | Check the fuel level by varying the value of the resistance as per the calibration table. Max resistance range changed to 1K ohm | Calibration table | FR 1, FR25 | GCU should display the fuel level as per the calibration table when the resistance is changed.
|  | Please disable Fuel display in Percentage from configuration | Fuel In Ltrs |  | On Fuel Level Screen Remaining fuel should be display in Liters | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
|  | Please Enable Fuel display in Percentage from Configuration | Fuel In Percentage |  | On Fuel Level Screen Remaining fuel should be display in Liters as well as Percentage | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-06
|  | Set the fuel theft alarm threshold. Monitor the fuel in litre and vary the fuel level below fuel consumption in next one hour. Note:- Engine should be OFF for above test. | Fuel Theft Warning. | FR 1 | When the fuel consumption is more than fuel theft threshold then GCU should declares Fuel theft Warning alarm at the end of 2nd hours. | Not tested in this build | Not tested in this build | Not tested in this build | Not tested in this build
3.Lube Oil Pressure Input
|  | Select the analogue input as a Lube oil pressure sensor. Enter the calibration table for the same and set the warning and shut down threshold for the LOP. Simulate the low oil pressure level by varying the pot connected to the input. | LOP warning and Threshold. | FR 1 | When the LOP level is below the warning threshold, GCU should give the warning for the Low Oil Pressure. When the Lop level becomes less than the shut down threshold, GCU should generate the shut down for the Low Oil Pressure.
|  | Disconnect the LOP connector from the GCU and check for the alarm. | Oil pressure circuit open | FR 45 | When the connector is removed from the GCU, GCU should display the alarm warning or shutdown, oil pressure circuit open. Or should not give alarm if none action is selected. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-07
|  | Vary the resistance from calibration table and check the oil pressure level . Max resistance range changed to 1K ohm | Calibration table | FR 1, FR 25 | GCU should display the LOP level according to the calibration table entered.
|  | Enable the pressure monitoring before crank. | High oil pressure detected | FR 1 | GCU should give high oil pressure detected warning & should not start the Genset. When condition gets cleared then the warining should be auto cleared.
4. Shelter temperature
|  | Check the shelter temperature by varying the value of the resistance as per the calibration table. Max resistance range changed to 1K ohm | Calibration table | FR 25 | GCU should display the shelter temperature as per the calibration table when the resistance is change.
|  | Disconnect the pot connected to the input and simulate the shelter temperature circuit open situation when the engine is ON as well as Off. | Circuit Open |  | When the shelter temperature circuit is open, then the GCU should generate the Notification alarm for the “ shelter temperature Circuit Open”. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-07
|  | Set the threshold value for High shelter temperature, vary temperature using resistance pot. | High shelter temperature alarm |  | When shelter temperature goes above its set threshold value then GCU should give high shelter temperature notification alarm | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-07
|  |  | Alarm recovery |  | When shelter temperature goes below its set threshold value then GCU should clear high shelter temperature notification alarm. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-07
5. S2 Sensor as Auxillary Sensor
|  | Check the S2 auxillary sensor by varying the value of the resistance as per the calibration table. Max resistance range changed to 1K ohm | Calibration table | FR 25 | GCU should the S2 sensor as per the calibration table when the resistance is change.
|  | Disconnect the pot connected to the input and simulate the S2 sensor circuit open situation when the engine is ON as well as Off. | Circuit Open |  | When the S2 sensor circuit is open, then the GCU should generate the S2 open circuit alarm for the and should take action as per set action | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-07
|  | S2 sensor -name string | Sensor Name |  | S2 sensor should have sensor name string, user can set sneor name of 20 charactors maximum. All alphanumric keywords and all special chractors should be acceptable. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-07
|  | 6. S3 Sensor as LOP Current Sensor |  | FR 26
|  | Select analogue input S3 as a LOP sensor. Enter the calibration table for the same and set the warning and shut down threshold for the LOP. | LOP warning and shutdown Threshold. |  | When the LOP level is below the warning threshold, GCU should give the warning for the Low Oil Pressure. When the Lop level becomes less than the shut down threshold, GCU should generate the shut down for the Low Oil Pressure. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-11
|  | Simulate LOP(4-20 mA) ciruit open by disconnecting connector from GCU. | oil pressure circuit open | FR 45 | When connector is disconnected from GCU then GCU should generate LOP-Circuit open alarm as warning or shutdown. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-11
|  | Simulate LOP(4-20 mA) ciruit by connecting connector to GCU. Simulate the recovery condition of open circcuit when Fuel voltage sensor is open or @1.5 v | oil pressure circuit open recovery |  | when the Connector is reconnected to theGCU, GCU should recover from open circuit condition and should show the respective reading. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-11
|  | Simulate LOP(4-20mA) over current by varying the value of current with pot and set it above 25mA | Over Value |  | GCU should generate LOP Sensor - Over value warning or shutdown as per action selected for open circuit alarm when current value goes above 25mA. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-11
|  |  | over value recovery |  | When the supply current decresed from 25 mA to 20 mA on Pin S3 then sensor should recover from over value condition and display reading according to the current applied . | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-11
|  | Set calibration table in GCU for LOP values | Calibration table | FR 39 | GCU should display correct value of pressure in bar. Current values in calibration table should have offset of 2 digits after decimal point.
|  | Give the voltage to S3 sensor pin above 7.7V approximately(ADC Count 4096) and check the LOP current screen. | Short to Battery |  | When the voltage above 7.7V given to S3 sensor Pin , GCU should give warning alarm as" Sensor S3 short to battery "and only display on LOP current mon screen as "Short to battery". | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-11
|  | Give within range input of LOP current to Pin S3, Simulate the recovery condition of short to battery when Fuel voltage sensor is open or @1.5 v | short to battery recovery |  | When short to battery condition is recovered and applied normal range voltage then also the monitoring screen should display short to battery when alarm acknowledge key ispressed with recovery then only LOP current monitoring screen should display the value of current | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-29
|  | Enable the pressure monitoring before crank. | High oil pressure detected |  | GCU should give high oil pressure detected warning & should not start the Genset. . When condition gets cleared then the warining should be auto cleared. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-11
|  | 7. S3 Sensor as LOP Voltage Sensor |  | FR 26
|  | Select the analogue input as a LOP voltage sensor. Enter the calibration table for the same and set the warning and shut down threshold for the LOP. Simulate the low oil pressure level by varying the pot connected to the input.Check that the respective alarms get logged on the MODBUS Map. | LOP warning and Threshold. |  | When the LOP level is below the warning threshold, GCU should give the warning for the Low Oil Pressure. When the LOP level becomes less than the shut down threshold, GCU should generate the shut down for the Low Oil Pressure. Shutdown and warning alarms should get logged on MODBUS Map. (RG-16384) | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-04-17
|  | Enable circuit fault , Disconnect the LOP connector from the GCU and check for the alarm. | Oil pressure circuit open | FR 45 | When the connector is removed from the GCU, GCU should give oil pressure open circuit alarm. As per action selected. Or should not give any alarm if none action is selected. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-11
|  | reconnect the LOP connecter to GCU and check the monitoring screen. Simulate the recovery condition of open circcuit when Fuel voltage sensor is open or @1.5 v | oil pressure circuit open recovery |  | when the Connector is reconnected to theGCU, GCU should recover from open circuit condition and should show the respective reading. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-11
|  | Vary the voltage and check the oil pressure level. | Calibration table | FR 39 | GCU should display the LOP level according to the calibration table entered. Voltage values in calibration table should have offset of 2 digits after decimal point.
|  | Enable the pressure monitoring before crank. Set the pressure level above the pressure sensor monitoring threshold. | High oil pressure detected |  | GCU should give high oil pressure detected warning & should not start the Genset. . When condition gets cleared then the warining should be auto cleared. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-11
|  | Set warning or shutdown action for circuit fault, Give the voltage to S3 sensor pin above 5.5V and check the LOP screen. | Over Value |  | When the supply voltage to sensor s3 pin goes above 5.5V, GCU should give warning or shut down alarm as per action selected in open circuit action alarm as "LOP Sensor over value" and also on LOP screen GCU should display over value. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-11
|  | Set None ation to circuit fault action, Give the voltage to S3 sensor pin above 5.5V and check the LOP screen. | Over Value |  | When the supply voltage to sensor s3 pin goes above 5.5V, GCU should not give alarm as "LOP Sensor over value" but LOP screen on GCU should display over value. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-11
|  |  | over value recovery |  | When the supply voltage decresed from 5.6 v to 5 v on Pin S3 then sensor should recover from over value condition and display reading according to the voltage applied . | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-11
|  | Give the voltage to S3 sensor pin above 7.7V approximately (ADC Count above 4096) and check the LOP screen. | Short to Battery |  | When the supply voltage to sensor s3 pin goes above 7.7V, GCU should give warning alarm as "Short to battery" and also on LOP screen GCU should display short to battery. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-06-20
|  | Simulate the recovery condition of short to battery also recover the condition when Fuel voltage sensor is open or @1.5 v | short to battery recovery |  | When the suppky voltage decresed from 7.7 v to 5 v on Pin S3 then sensor should recover from short to battry condition and display reading according to the viltage applied , if voltage is above 5.5V then GCU should display over value on screen | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-06-20
|  | 8. S4 Sensor as Fuel Voltage Sensor |  | FR 27
|  | Select the analogue input as a Fuel voltage sensor and enter the calibration table for the same. Set the warning and shut down threshold for LFL. Simulate the Low fuel level by varying the pot connected to the analogue inputs. | Low Fuel Level Warning and Shut down |  | When the fuel level is below the warning threshold, GCU should give the warning for the LFL. When the Fuel level becomes less than the shut down threshold, GCU should generate the shut down for the LFL. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-12
|  | Check the fuel level by varying the value of the voltage as per the calibration table. | Calibration table | FR 39 | GCU should display the fuel level as per the calibration table when the voltage is changed.Voltage values in calibration table should have offset of 2 digits after decimal point.
|  | Set the fuel theft alarm threshold. Monitor the fuel in litre and vary the fuel level below fuel consumption in next one hour. Note:- Engine should be OFF for above test. | Fuel Theft Warning. | FR 1 | When the fuel consumption is more than fuel theft threshold then GCU should declares Fuel theft Warning alarm at the end of 2nd hours. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-12
|  | Disconnect the sensor S4 connector from the GCU and check for the alarm. | Open circuit |  | GCU should not give alarm of open circuit even if Sensor s4 is open but GCU should display open circuit on Fuel level screen. | NA | NA | NA | NA | NA | NA | NA
|  | reconnect the LOP connecter to GCU and check the monitoring screen. Simulate the recovery condition of open circcuit when Fuel voltage sensor is open or @1.5 v | Fuel circuit open recovery |  | when the Connector is reconnected to theGCU, GCU should recover from open circuit condition and should show the respective reading. | NA | NA | NA | NA | NA | NA | NA
|  | Give the voltage to S4 sensor pin above 5.0V and check the Fuel level screen. | Over Value |  | When the supply voltage to sensor S4 pin goes above 5.0V, GCU should display "over value" on Fuel screen and should not give alarm of over value. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-11
|  |  | over value recovery |  | When the supply voltage decresed from 5.6 v to 5 v on Pin S4 then sensor should recover from over value condition and display reading according to the voltage applied . | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-11
|  | Give the voltage to S4 sensor pin above 7.7V approximately(ADC Count 4096) and check the Fuel Level screen. | Short to Battery |  | When the supply voltage to sensor s4 pin goes above 7.7V, GCU should not give alarm and only display on Fuel level screen as "Short to battery". | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-04-01
|  | Simulate the recovery condition of short to battery also recover the condition when Fuel voltage sensor is open or @1.5 v | short to battery recovery |  | When the supply voltage decresed from 7.7 v to 5 v on Pin S4 then sensor should recover from short to battery condition and display reading according to the voltage applied , if voltage id above 5.5 then GCU should display over value on screen | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-04-01
21 | GCU_21 | Digital Inputs. and Analog as Digital inputs
All the Digital Input sources can be assigned to the particular input source. Check each source for each of the Input viz DIG IN A, B, C, D, E, F, G, H, I ,Q, R and Analog as Digital J, K, L, M, N, O, P. The test cases for the different sources are as described below. Polarity of the input may can be set as “Open to activate” or “Close to activate”. Inputs need to be tested for both Open to activate and close to activate polarities,
|  | User Configured | User Configured
|  | Select the digital input as a user configured, assign the name for it through the GUI. Select the polarity for the activation and the action. Also select the activation delay for the digital input. |  | FR 1 | When the input is selected as an user configured, then after activating this input, GCU should display the alarm of auxiliary input occured . If the string name for the input is entered from the GUI, then it should display that string when the input is activated.
|  | Low fuel level switch. | Low fuel level switch.
|  | a)Assign the DIG IN as a Low fuel level switch and the polarity for activation. Select the action for the LFL switch. Select the activation delay and the monitoring period for the Input switch. Activate the input as per the polarity set. |  | FR 1 | GCU should generate the selected action’s alarm if the input is activated for the activation delay.
|  | Oil pressure switch | Low oil pressure switch
|  | a)Assign the DIG IN as a LOP switch and the polarity for activation. Select the action for the LLOP switch. Select the activation delay and the monitoring period for the Input switch. Activate the input as per the polarity set. |  | FR 1 | GCU should generate the selected action’s alarm if the input is activated for the activation delay.
|  | High temperature switch | High temperature switch
|  | a) Assign the DIG IN as a temperature switch. Select the action after the activation of the switch. select the activation delay and the monitoring period. Activate the input by keeping it open or by grounding it as per the polarity |  | FR 1 | GCU should generate the selected action’s alarm if the input is activated for the activation delay.
|  | Low Water level switch | Water level switch
|  | a) Assign the DIG IN as a water level switch. Select the action for the Water level switch from the water level monitoring field. Set the activation delay. Select the polarity of the activation and activate the input as per the polarity. |  | FR 1 | GCU should generate the selected action’s alarm if the input is activated for the activation delay.
|  | Emergency stop | Emergency Stop
|  | a) Assign the DIG IN as an Emergency stop. Select the polarity for the activation. |  | FR 1 | When input is activated, GCU should stop immediately without any cooling down.
|  | Remote start/stop | Remote Start/Stop
|  | a) Assign the DIG IN as a Remote Start. Keep the GCU in the AUTO mode. Select the polarity for the activation.Disable mains monitoring |  | FR 1 | GCU should be in the AUTO mode. When input is activated, GCU should Start. GCU should be ON as long as this input is activated. GCU should stop as soon as the input is deactivated.
|  | Simulate start | Simulate Start
|  | a) Assign the DIG IN as a Simulate start. GCU should be in manual mode. Select the polarity for the activation. |  |  | When input is activated, GCU should Start & remains ON after deactivating the input and should not stop until STOP command is given or any Shut Down or Electrical trip alarm is Active.
|  | Simulate stop | Simulate Stop | FR 1
|  | a) Assign the DIG IN as a Simulate stop. Keep the GCU in the manual mode. Select the polarity of the activation. Keep the GCU ON before activating this input. |  |  | GCU should stop when this input is activated.
|  | Simulate Auto | Simulate AUTO | FR 1
|  | a) Assign the DIG IN as a Simulate auto. Keep the GCU in the manual mode. Select the polarity of the activation. |  |  | GCU should enter in the auto mode when this input is activated. Then GCU should perform all the functions related to the AUTO mode.
|  | Close generator, Open mains | Close generator, Open mains | FR 1
|  | a) Assign the DIG IN as Close generator, Open mains & digital output as a Close GCU contactor. |  |  | This input should work in the manual mode & engine ON condition only. When this input is activated, GCU should close the Genset contactor and open the mains contactor.
|  | Open generator, Close mains | Open generator, Close mains | FR 1
|  | a) Assign the DIG IN as Open generator, Close mains & digital output as Close mains contactor. |  |  | This input should works in the manual mode & engine ON condition only. When this input is activated, GCU should close the mains contactor and open the Genset contactor.
|  | Simulate mains | Simulate mains | FR 1
|  | a) Assign the DIG IN as a simulate mains. Select the polarity of the activation. Activate the input as per the polarity of the activation. |  |  | When Input is activated, GCU should operate as the mains is Healthy. It should remain Healthy even though the mains is cut off.
|  | V-Belt Broken | V-Belt Broken switch | FR 1
|  | a) Assign the DIG IN as an V-Belt broken. Select the action for the Input. Assign any name for the Input and select the polarity of the activation. |  |  | GCU should generate the selected action’s alarm if the input is activated for the activation delay. GCU should display V-belt broken alarm.
|  | Mains contactor latched | Mains contactor latched | FR 1
|  | Check this input source only in manual mode SMD start/stop as explained above. Configured : CT location- On Load Cable |  |  | When mains contactor is latched & input is activated mains kwh, kvah & run time should be increased. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-04-19
|  | Genset contactor latched | Genset contactor latched
|  | Check this input source only in manual mode SMD start/stop as explained above. Configured : CT location- On Alt Output Cable |  |  | When Genset contactor is latched & input is activated Genset kwh, kvah & kvarh should be increased. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-04-19
|  | Battery Charger | Battery Charger
|  | Assign the input source as a Battery charger . Select the polarity of the activation. Activate the input when the mains is healthy. Also, activate the input when the mains unhealthy as well. |  |  | When the battery charger is activated while mains is healthy, GCU should generate the alarm of Battery Charger . Input does not work in case of mains unhealthy.
|  | Smoke Fire | Smoke Fire
|  | Assign the input source as a Smoke fire. Activate the input when the GCU is running. |  |  | When the smoke fire input is activated, GCU should generate the alarm and take the action accordingly.
|  | Mode selector switch | Mode select switch
|  | Assign the input source as a Mode select switch. |  |  | When mode select switch is assign as input source then Facia key of GCU for mode change Auto, manual should not work, When GCU is in manual mode then only start, stop facia key should work. when mode selectcor switch input is activated once then mode should be chaged , and when deactivated then again mode is switched. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-07
|  | Ambient temprature switch | Ambient temp switch
|  | Assign the input source as a Ambient temprature switch. Keep Ambient temp enable checkbox enable in engine >>preheat selction. |  | FR 23 | This input should work with preheat functionality only , when prehating with ambient temp switch is enabled and ambient temp switch is active then only preheat Functionality should work and device should run preheat timer after start delay when switch is deactivated during prehat timer then GCU should skip the preheat timer should start cranking ,when switch is not active and start command is received by GCU then GCU should skip preheat timer. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-07
|  | Super Capacitor Fail | Super Capacitor Fail / Enable BTS monitioring |  | When the input is selected as an user configured, then after activating this input, GCU should display the alarm of auxiliary input occured . If the string name for the input is entered from the GUI, then it should display that string when the input is activated. | Not tested in this build | Same as expected | Not tested in this build | Not tested in this build | Pass | Sangeet Wankhede | 2024-06-18
22 | GCU_22 | Digital Outputs.
|  | Rig test, LEDs are used to check the status of the O/P. Any Output from A to F can be assigned to any one of the output source and polarity can be et as an “Active High' or “Active Low”. Depending upon the polarity, LEDs at the output will either glow or will be OFF. Output sources are as follows. | OUTPUTS
|  | Sounder alarm |  | FR 1 | If any alarm (warning, ET, SD) is generated, this output should go high. This output should remain activated as long as the sounder alarm timer is running.
|  | Battery Over Voltage |  | FR 1 | Output should be active when the Battery over voltage alarm is pending.
|  | Battery under Voltage |  | FR 1 | Output should be active when the Battery under voltage alarm is pending.
|  | Charge Alternator shut down |  | FR 1 | Output should be active when the Charge shut down alarm is generated.
|  | Charge Alternator Warning |  | FR 1 | Output should be active when the Charge warning alarm is generated.
|  | Close generator contactor |  | FR 1 | a)The output should be active when the Genset is running and GCU issues the command for latching the Genset contactor b) The output should be active when the digital input “Close genset/open mains” is active in the manual mode.
|  | Close mains contactor |  | FR 1 | a) Output should be active when the mains is healthy and GCU issues the command for latching the mains contactor. b) The output should be active when the digital input “Close mains/open generator” is active.
|  | Mains ure |  | FR 1 | Output should be active when mains is unhealthy.
|  | Common Alarm |  | FR 1 | Output should be active when any alarm is pending except notification.
|  | Common Electrical Trip |  | FR 1 | Output should be active when any electric trip alarm is pending.
|  | Common shut down |  | FR 1 | Output should be active when any shut down alarm is generated.
|  | Common Warning |  | FR 1 | Output should be active when any warning is generated.
|  | Cooling down |  | FR 1 | Output should be active during the cooling down for the time specified in the cooling down timer.
l |  | DIG IN A |  | FR 1 | Output should be active when the DIG IN A is active.
|  | DIG IN B |  | FR 1 | Output should be active when the DIG IN B is active.
|  | DIG IN C |  | FR 1 | Output should be active when the DIG IN C is active.
|  | DIG IN D |  | FR 1 | Output should be active when the DIG IN D is active.
|  | DIG IN E |  | FR 1 | Output should be active when the DIG IN E is active.
|  | DIG IN F |  | FR 1 | Output should be active when the DIG IN F is active.
|  | DIG IN G |  | FR 1 | Output should be active when the DIG IN G is active.
|  | DIG IN H |  | FR 1 | Output should be active when the DIG IN H is active.
|  | DIG IN I |  | FR 1 | Output should be active when the DIG IN I is active.
|  | DIG IN J |  | FR 1 | Output should be active when the DIG IN J is active.
|  | DIG IN K |  | FR 1 | Output should be active when the DIG IN K is active.
|  | DIG IN L |  | FR 1 | Output should be active when the DIG IN L is active.
|  | DIG IN M |  | FR 1 | Output should be active when the DIG IN M is active.
|  | DIG IN N |  | FR 1 | Output should be active when the DIG IN N is active.
|  | DIG IN O |  | FR 1 | Output should be active when the DIG IN O is active.
|  | DIG IN P |  | FR 1 | Output should be active when the DIG IN P is active.
|  | DIG IN Q |  | FR 1 | Output should be active when the DIG IN O is active.
|  | DIG IN R |  | FR 1 | Output should be active when the DIG IN P is active.
|  | Emergency Stop |  | FR 1 | Output should be active when the Emergency stop is executed.
|  | Stop Solenoid |  | FR 1 | Output should be active when the stop solenoid output is high.
|  | FAIL to Start |  | FR 1 | Output should be active when the to start alarm is generated.
|  | FAIL to Stop |  | FR 1 | Output should be active when the to stop alarm is generated.
|  | Fuel Relay |  | FR 1 | Output should be active when the Fuel relay is ON.
|  | Generator Available |  | FR 1 | This output should become active when engine crank disconnect successfully and warmup delay completed.
|  | R OV Shut down |  | FR 1 | Output should be active when the R phase over voltage alarm is generated. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-07
|  | R UV Shut down |  | FR 1 | Output should be active when the R phase under voltage alarm is generated. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-07
|  | Y OV Shut down |  | FR 1 | Output should be active when the Y phase over voltage alarm is generated. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-07
|  | Y UV Shut down |  | FR 1 | Output should be active when the Y phase under voltage alarm is generated. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-07
|  | B OV Shut down |  | FR 1 | Output should be active when the B phase over voltage alarm is generated. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-07
|  | B UV Shut down |  | FR 1 | Output should be active when the B phase under voltage alarm is generated. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-07
|  | Generator Over Current |  | FR 1 | Output should be active when the Generator over current alarm is executed by the GCU. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-07
|  | High Temp |  | FR 1 | Output should be active when the High temp alarm is activated.
|  | Low fuel level |  | FR 1 | Output should be active when the LFL alarm is activated through digital switch or analog sensor alarm
|  | Low fuel level Notification |  | FR 49 | Output should be active only when the Low fuel notificaton alarm is activated through sensor. And should not glow for digital switch alarm. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-07
|  | Low oil pressure |  | FR 1 | Output should be active when the LLOP or LOP sensor alarm is activated.
|  | Mains voltage high |  | FR 1 | Output should be active when the mains voltage is higher than the threshold value.
|  | Mains voltage low |  | FR 1 | Output should be active when the mains voltage is lower than the threshold value.
|  | Oil pressure ckt. Open |  | FR 1 | Output should be active when the oil pressure open circuit alarm is activated.
|  | open generator contactor |  | FR 1 | a) Output should be active when the input “Close mains/open generator” is activated. b) Output should be active when the load is to be transferred on the mains if the Genset is in the AMF mode.
|  | open mains contactor |  | FR 1 | a) Output should be active when the input “Close genset/open mains” is activated. b) Output should be active when the load is to be transferred on the Genset.
|  | Over Frequency shut down |  | FR 1 | Output should be active when the OF shut down is executed.
|  | Over Speed shut down |  | FR 1 | Output should be active when the OS shut down is executed.
|  | Gross Over Speed shut down |  | FR 1 | Output should be active when the gross Over Speed shut down alarm is generated.
|  | Start Relay |  | FR 1 | Output should be active when the Start relay is ON during Engine Start ie during crank time.
|  | Temperature Sensor Open Ckt |  | FR 1 | Output should be active when the temperature circuit open alarm is activated.
|  | Under Frequency Shut down |  | FR 1 | Output should be active when the UF shut down is executed.
|  | Under Speed Shut down |  | FR 1 | Output should be active when the US shut down is executed.
|  | Maintenance Due |  | FR 1 | Output should be active when the maintenance alarm is pending.
|  | Stop mode |  | FR 1 | Output should be active when the GCU is STOP.
|  | Auto mode |  | FR 1 | Output should be active when the GCU is in the AUTO mode.
|  | Manual mode |  |  | Output should be active when the GCU is in the MANUAL mode.
|  | Preheat Output |  |  | Output should be active when the preheating is ON ie during the preheat timer is running.
|  | ECU start |  | FR 34 | Output should be active when start command is received by GCU and active till DG is ON, and should deactivate when stop command is received and DG is stopped, the output should be active in to stop condition | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-07
|  | Malfunction indicator lamp |  | FR 33 | Otput should be active when command is send from DM01 resister | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-04-01
23 | GCU_23 | TIMERS
|  | Refer sheet three for the timer functionality and the rest cases. Observe the modules and the expected results mentioned in the Sheet. | Timer modules | FR 1 | Refer to the sheet 3 for the timer related test cases and the results. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-06
24 | GCU_24 | Alternator Configurations
|  | Select the alternator fitted as a NO. Start the Genset and create any alternator related alarm. | Alternator Fitted selection | FR 1 | When the alternator fitted is selected as a NO, then GCU should avoid all the alternator related alarms. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-06
|  | Set the number of poles from the configuration menu. Select the speed sensing source as an Alternator Frequency. Start the Genset and check the RPM. | Number of poles | FR 1 | Assuming that the alternator frequency is 50Hz, GCU should calculate the RPM as 120f/p. So, for 2 poles, RPM should be 3000, for 4 poles it should be 1500, for 6 poles, it should be 1000 and for 8 poles , it should be 750. | Working as Expected. | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-06
|  | Select the alternator system as 1 phase first and then select as a 3 phase. Check the monitoring screens in both cases. | Alternator System | FR 1 | When the system is selected as a 1 phase, then the GCU should display the single phase (PH-N) voltage of the Genset. When it is selected as a 3 phase, then GCU should display both PH-PH and PH-N voltages of all 3 phases. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-06
|  | Set the minimum healthy voltage and minimum healthy frequency of the Alternator. Select the output A as a Gen available. Select the contactor outputs and start the GCU. | Minimum healthy voltage and minimum healthy frequency | FR 1 | The output Gen available should not go high as long as the minimum healthy voltage and minimum healthy frequency are reached. Also, the Genset contactor should get latched after the Gen available output goes high. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-06
|  | Enable the phase reversal detection. Connect the phases of the Genset in reverse order to the GCU input. Start the Genset and check for the alarm. | Phase reversal detection | FR 1 | Phase reversal Should be detected when Gen ON is detected (immidiate after crank disconnect), then the GCU should generate the alarm and should take the action as per the configuration. Refer the sheet 'Phase Sequence' for the different combinations of the RYB sequences. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-06
|  | Enable the phase reversal detection & Set the appropriate action. Connect the phases of the Genset in reverse order to the GCU input. Start the Genset and check for the alarm. | Phase reversal Action | FR 1 | When the phase reversal is detected, then the GCU should generate the alarm and should take the action as per the configuration. Refer the sheet 4 for the different combinations of the RYB sequences. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-06
|  | Set Auto Load Transfer enable/disable also put GCU in manual mode. | Auto Load Transfer | FR 1 | If Auto load transfer is disabled, start GCU but load on Genset should not be latched. If Auto load transfer is enabled, start GCU should latch load on Genset. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-06
|  | Enable/Disable the monitoring of alternator waveform detection. To sense Alternator waveform or Mains waveform. Note:-Keep No of poles of alternator 4. and under speed threshold | Alternator Wave Detection | FR 1 | Temper Run time screen should be added. If Mains is connected to Genset connector, GCU give Invalid Run alarm & should increase Kwh & Run time of Temper Run time screen. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-06
25 | GCU_25 | Voltage Monitoring
|  | a) Enable the under voltage shut down and set the threshold value for the UV shut down. Connect the Genset input to the GCU through the variac on the rig. Decrease the Genset voltage with the help of variac. | UV shut down | FR 1 | GCU should execute the shut down when the DG voltage is less than the threshold value.
|  | b) Enable the under voltage warning and set the threshold value for the UV warning. Vary the Genset voltage with the help of the variac. | UV warning | FR 1 | GCU should execute the warning alarm when the DG voltage falls below the threshold value.
|  | c) Enable the over voltage shut down. Set the threshold value for the Over voltage shut down. Increase the Genset voltage with the help of the variac. | OV shut down | FR 1 | GCU should execute the OV shut down when the DG voltage becomes greater than the threshold value.
|  | d) Enable the OV warning and set the OV warning threshold value. Increase the Genset voltage with the help of the variac. | OV warning | FR 1 | GCU should give the warning when the DG voltage is greater than the threshold value.
26 | GCU_26 | Frequency Monitoring
|  | a) Enable the under frequency shut down and set the threshold value for the UF shut down. Disable the speed monitoring for this test. Disconnect the Genset input from the GCU to simulate the UF situation | UV shut down | FR 1 | GCU should execute the shut down when the DG frequency is less than the threshold value.
|  | b) Enable the under frequency warning and set the threshold value for the UF warning. Disable the speed monitoring for this test. Disconnect the Genset input from the GCU to simulate the UF situation | UV warning | FR 1 | GCU should execute the warning alarm when the DG frequency falls below the threshold value.
|  | c) Enable the over frequency shut down. Set the threshold value for the Over frequency shut down below 50 to simulate the OF situation. | OV shut down | FR 1 | GCU should execute the OV shut down when the DG frequency becomes greater than the threshold value.
|  | d) Enable the over frequency warning. Set the threshold value for the Over frequency warning below 50 to simulate the OF situation. | OV warning | FR 1 | GCU should give the warning when the DG frequency is greater than the threshold value.
2 | GCU_27 | Current Monitoring
|  | Generator current rating | Full load current |  | Generator load current capacity prescribed by the generator manufacturer.Full load current unit is Amp/phase and range is 1-800Amp | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-08
|  | a) For some specific load, check the current in the Genset. Set over current threshold less than the current measured for that load. | Over current threshold and Full load rating | FR 1 | GCU should give the warning or electrical trip or shut down as per the action selected, when the current is greater than threshold value per phase. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-08
|  | b) Set the over current delay. | Over current delay | FR 1 | GCU should give the over current alarm only if the over current situation lasts for the over current delay. Over current delay should have maximum range 800 sec | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-08
|  | c) Select the alternator system as 3 phase. Set the load unbalanced threshold action. Apply the load on the all three phases. Disconnect the load of any one phase. | Unbalance Load Action | FR 1 | GCU should give the unbalanced load alarm and execute the action. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-08
|  | d) Set the load unbalanced threshold. Apply the load on the all three phases for unbalanced situation. Set Load unbalanced delay | Unbalanced Load Delay | FR 1 | GCU should generate unbalanced load alarm after unbalanced load delay expire. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-08
|  | F) Select the alternator system as 3 phase. Set the Full load current value= max value of current / per pahse .Set the load unbalanced threshold. Apply the load on the all three phases set the unbalance activation threshold. | Unbalance Load Threshold/ Unbalanced load activation threshold | FR 47 | GCU should calculate unbalanced load alarm only if both activation threshold is less than actual load percentage the unbalanced load threshold. 1st condition unbalance load threshould calculation = (Max current out of 3 phases- Min current out of 3 phases / Rated current per phase ) *100 and for 2nd threshold unbalance activation thresshold = % current for any of one phase out of 3 phases is over the set activation threshold. and % current calculation considering on Full Load Current i.e calculation= (Unbalanced load Act threshold* Full load current)/100. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-08
S |  | c) Select the alternator system as 3 phase. Set the load unbalanced threshold and unbalnced load act threshold. 1. Apply the load on the all three phases. Check whether 1) (max I - min I)/ rated I per phase > unbalanced load threshold 2) Here range of unbalanced load activation threshold should vary 50-100% | Unbalance load alarm | FR 47 | GCU should give the unbalanced load alarm when 1) The actual load unbalanced is greater than set unbalanced load threshold. 2) Unbalanced load gests triggered when any pahse of current is greater than Unbalanced Load Activation threshold percentage of full load current. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-08
|  | Set the CT calibration factor as 1.000 first from the GUI. Start the Genset and measure the current. Then set the different values of the CT calibration factor and check the current displayed by the GCU for each value. | CT calibration factor | FR 1 | GCU should display the current as per the CT calibration factor set from the GUI. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-08
|  | Set the CT location and then observe the monitoring screens for the mains load and current. | CT location | FR 1 | When the CT location is set as “On load cable”, then GCU should display the mains KW and KWH screens. Also GCU should measure the mains current and KW. When the CT location is set as “On alternator cable”, then GCU should not count the mains KW and current. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-08
28 | GCU_28 | Earth Leakage current monitoring
|  | Connect the earth CT input to the GCU. Set the CT ratio for the earth leakage current CT. one of the phase through the earth CT to simulate the current flowing through neutral. Set the threshold for the leakage current and action for the leakage current. |  | FR 11 | If the current flowing through the earth CT is greater than the threshold set, then GCU should issue the alarm and should take the action as per the configurations. | Not tested in this build | Not tested in this build | Working as expected | Not tested in this build | Pass | Sangeet W. | 2024-06-19
29 | GCU_29 | Load Monitoring
|  | a) Set the generator rating in the GUI. Increase the load on the Genset step by step. | Generator rating | FR 1 | GCU should display the generator rating as entered from the GUI. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-08
|  | b) Select the overload action and increase the load above the rating. | Overload action. | FR 1 | GCU should execute action as per the selected action in the overload action field. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-08
|  | c) Set the overload threshold value. | Overload threshold | FR 1 | GCU should execute the overload action when the load crosses the percentage threshold of the full load rating. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-08
|  | d) Set the overload delay. | Overload Delay | FR 1 | GCU should execute the overload alarm only if the Overload situation remains for the more than this delay. Delay max value should be 60 sec. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-08
|  | e) Set load percent above 101% of the rated load and below Overload Trip Threshold start the Engine and let the enigne run for 1 hr continously. | Extended overlaod Trip action | FR1 | GCU should take the Extended overlaod Trip action if the set load percent is above the 101% of rated laod and Engine is running for 1 hrs. | Not tested in this build | Working as expected | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-06-13
|  | f) Set load percent above 101% of the rated load and below Overload Trip Threshold start the Engine and let the enigne run for intermediate cycle of (15 mins x 4 cycle's or 10 mins x 6 cycle's)for the total time of 1 hr in betwwen the 12hrs. | Extended overlaod Trip action | FR1 | GCU should take the Extended overload Trip action if the set load percent is above the 101% of rated load here GCU should calculate Extended Overload Run Hours as mentioned in test case while engine is running for the total time with intermediate run hours count as 1hr. | Not tested in this build | Working as expected | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-06-13
|  | h) After the Extended Overload trip alarm appears on GCU, let the engine take start command after the alarm is acknowledged. | Extended overlaod Trip with ACK in reset time | FR1 | After the Extended Overload trip alarm appear on GCU screen. Engine can be start only if load is below 100% or the reset time period is completed i.e after 12hrs. | Not tested in this build | Working as expected | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-06-13
|  | h) After the Extended Overload trip reset time i.e 12hrs is over start the engine normally. | GCU should start Normally. | FR1 | After the Extended Overload trip when the reset time period is over i.e 12hrs Engine will start normally and no alarm should appear on GCU screen. | Not tested in this build | Working as expected | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-06-13
30 | GCU_30 | Mains Monitoring
|  | a) Select the mains as a 1PH or 3Ph and observe the screens of the mains monitoring. Disable the 3 phase calculation parameter. | Mains AC system | FR 1 | When the mains is selected as a 1PH, then on the home screen, it should display the L-N voltage of the L1 phase only. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-06
|  | a) Select the mains as a 1PH and observe the screens of the mains monitoring enable the 3 phase calculation parameter. |  |  | When mains is selected as a 1 phase and 3 phase calculation is enabled then then the screen should display the voltages of the all 3 phases and should calculate current KWH and Kvah for all 3 phases | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-11
|  | Select the mains as a 3Ph and observe the screens of the mains monitoring. |  |  | When the mains is selected as a 3PH, then the screen should display the voltages of the all 3 phases. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-06
|  | Select mains as a 1PH and enable the 3 phase calculation parameter, CT connection should be on load cable |  | FR 35 | When the mains is selected as a 1PH and 3phase calculation parameter is enabled then the screen should display the voltages of the all 3 phases and GCU should calculate the KWh, Kvah for all 3 phases | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-11
|  | b) Connect the phases of the mains as per the sequences given in the Sheet 4. Check for the phase reversal alarm. | Phase reversal alarm | FR 1 | GCU should generate the alarm for the reversed phase sequences. The correct sequences and wrong sequences are mentioned in the Sheet 4. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-08
|  | c) Enable the under voltage monitoring and set the values of the TRIP and RETURN. | UV monitoring | FR 1 | GCU should take the action for the under voltage only if the UV monitoring is enabled. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-08
|  | d) Vary the mains voltage through the variac so as to reduce it below the trip value. | UV Trip. | FR 1 | GCU should cut the mains off and Mains fail should be declare. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-11
|  | e) Increase the voltage of the mains until it crosses the Return voltage. | UV Return | FR 1 | GCU should stop the DG and close the mains contactor after the mains detect delay. DG should be running when the voltage is between the trip and return values. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-11
|  | f) Enable the Over Voltage monitoring on and set the Trip and return values for the Over voltage. | OV monitoring | FR 1 | GCU should take the action for the over voltage only if the OV monitoring is enabled. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-08
|  | g) Increase the mains voltage through the variac so as to increase it above the trip value. | OV Trip. | FR 1 | GCU should cut off the mains supply and DG should get started after the mains detect delay. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-11
|  | h) Decrease the mains voltage below the return value. | OV Return | FR 1 | Mains should be healthy when Voltage is increasing from Return to trip value and When Mains voltage decreases from Trip value to return then Mains voltage should be unhealthy till value is below return value. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-11
|  | i) Enable the under Frequency monitoring and set the values of the TRIP and RETURN. when overall phase- phase value is under the set threshold which displayed on Home screen. | UF monitoring | FR 1 | GCU should take the action for the under Frequency only if the UF monitoring s enabled. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-11
|  | j) Vary the mains Frequency through the VFD so as to reduce it below the trip value. | UF Trip. | FR 1 | GCU should cut the mains off and DG should get started after the mains detect delay. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-11
|  | k) Increase the Frequency of the mains until it crosses the Return Frequency. | UF Return | FR 1 | GCU should stop the DG and close the mains contactor after the mains detect delay. DG should be running when the Frequency is between the trip and return values. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-11
|  | l) Enable the Over Frequency monitoring on and set the Trip and return values for the Over Frequency. when overall phase- phase value is over the set threshold which displayed on Home screen. | OF monitoring | FR 1 | GCU should take the action for the over Frequency only if the OF monitoring is enabled. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-11
|  | m) Increase the mains Frequency through VFD so as to increase it above the trip value. | OF Trip. | FR 1 | GCU should cut off the mains supply and DG should get started after the mains detect delay. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-11
|  | n) Decrease the mains Frequency below the return value. | OF Return | FR 1 | GCU should stop the DG and close the mains contactor after the mains detect delay. DG should be running when the Frequency is between the trip and return values. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-11
31 | GCU_31 | Crank Disconnect
|  | a)Set the crank attempts in the GUI. Disconnect the DG input from the GCU on the RIG. Give the start command. | Crank Attempts | FR 1 | GCU should give the number of crank attempts as set in the GUI. Start LED should be blink for the crank time & Crank rest time. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-04
|  | b) Enable the crank disconnect oil pressure field and set the crank disconnect pressure threshold. Give the start command by setting the oil pressure below the threshold. Increase the pressure by varying the pot. Disable alternator related alarms and select Alternator fitted as NO during this test. | Crank Disconnect On Oil Pressure | FR 1 | GCU should stop cranking when the oil pressure becomes more than the disconnect threshold value. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-05
|  | c) Set the Speed and frequency for the crank disconnect. Start the DG and maintain the frequency above the threshold by moving the actuator manually. | Crank Disconnect frequency. | FR 1 | GCU should stop the cranking when the frequency is higher than the threshold value. | Not tested in this build | Same as expected | Not tested in this build | Not tested in this build | Pass | Sangeet Wankhede | 2024-06-20
|  | d) Follow the same procedure as explained above by setting the crank disconnect Speed. | Crank Disconnect Speed | FR 1 | GCU should stop the cranking when the speed is higher than the threshold value. The maximum limit for the crank disconnect speed should be 800RPM. | Not tested in this build | Same as expected | Not tested in this build | Not tested in this build | Pass | Sangeet Wankhede | 2024-06-20
|  | e) Set the threshold for the crank disconnect voltage of the charging alternator voltage. | Crank Disconnect on charging alternator voltage | FR 1 | GCU should stop the cranking attempts when the pin is disconnected from the ground as the voltage across it will rise above the threshold value. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-04
|  | f) Enable the crank disconnect oil pressure field and set the crank disconnect pressure threshold. Give the start command by setting the oil pressure above the threshold. Increase the pressure by varying the pot and switch. Disable alternator related alarms and select Alternator fitted as NO during this test. | Enable Monitoring before crank (Resistive and current , voltage sensor and switch) | FR 2 | GCU should give High oil pressure detected (sensor) alarm and should not take the start action until alarm is cleared, . When condition gets cleared then the warining should be auto cleared. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-05
32 | GCU_32 | Speed Monitoring
|  | a) Enable the under speed shut down. Set the under speed threshold and decrease the speed below the threshold value. | Under speed shut down and Under speed threshold | FR 1 | GCU should shut down the DG if the speed is below the threshold value of the under speed.
|  | b) Set the under speed delay from the GUI. | Under Speed Delay | FR 1 | GCU should execute the shut down only if the DG runs at the under speed for time more than this delay after safety Mon delay over. If the DG reattains its normal speed before this delay is over, GCU should not execute the shut down. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-11
|  | c) Set the over speed threshold and increase the speed above the threshold value. | Over Speed Threshold | FR 1 | GCU should shut down the DG if the speed is greater than the threshold value of the over speed.
|  | d) Set the over speed delay from the GUI. | Over speed Delay | FR 1 | GCU should execute the shut down only if the DG runs at the over speed for time more than this delay. If the DG reattains its normal speed before this delay is over, GCU should not execute the shut down. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-11
|  | e) set the limit for the gross over speed alarm in the percentage. | Gross Over speed | FR 1 | When the speed of the DG becomes greater than the percentage value of the actual over speed threshold, then GCU should shut down the DG suddenly without taking any delay.
33 | GCU_33 | Battery Monitoring
|  | a) Select the action (Warning/Electric Trip/Shutdown/Notification) for the low battery voltage. Connect the variable DC power supply to the GCU and decrease the voltage below threshold value. | Low battery voltage action | FR 1 | GCU should execute the warning, shut down as per the action selected for the low battery voltage. | Not tested in this build | Working as expected | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-06-11
|  | b) Set the delay for the low battery voltage. Decrease the battery voltage below the threshold value and observe the time required foe GCU for generating alarm. | Low battery voltage delay | FR 1 | GCU should execute the low battery voltage alarm if the battery voltage remains less than the threshold value for time period set in the delay field. | Not tested in this build | Working as expected | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-06-11
|  | c) Select the action as (Warning/Electric Trip/Shutdown/Notification) for the low battery voltage & assign any one Digital output as Battery Unhealthy for the low battery voltage. Observe the Output along with GCU to generate the alarm. | Low battery voltage action with Assigned Digital output high | FR 1 | GCU should execute the low battery voltage if the battery voltage remains less than the threshold value & assigned Digital ouput should be high. | Not tested in this build | Working as expected | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-06-11
|  | d) Select the action (None) for the low battery voltage & assign any one Digital output as Battery Unhealthy for the low battery voltage. Observe the Output along with GCU to generate the alarm. | shoul not take Low battery voltage action but Assigned Digital output should be high | FR 1 | GCU should not execute the low battery voltage if action is selected as none, even the battery voltage remains less than the threshold value & but assigned Digital ouput should be high. | Not tested in this build | Working as expected | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-06-11
|  | e)Select the action for the High battery voltage. Increase the voltage of DC power supply above the threshold value. | High battery voltage action | FR 1 | GCU should execute the warning, shut down as per the action selected for the High battery voltage. | Not tested in this build | Working as expected | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-06-11
|  | f) Set the delay for the high battery voltage. Observe the time required for the GCU to generate the alarm. | High battery voltage delay | FR 1 | GCU should execute the high battery voltage if the battery voltage remains more than the threshold value for time period set in the delay field | Not tested in this build | Working as expected | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-06-11
|  | g) Select the action for the high battery voltage & assign any one Digital output as Battery Unhealthy for the high battery voltage. Observe the Digital output along with GCU to generate the alarm. | High battery voltage action with Assigned Digital output high | FR 1 | GCU should execute the high battery voltage if the battery voltage remains more than the threshold value & assigned Digital ouput should be high. | Not tested in this build | Working as expected | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-06-11
|  | h) Select the action (None) for the high battery voltage & assign any one Digital output as Battery Unhealthy for the high battery voltage. Observe the Output along with GCU to generate the alarm. | shoul not take High battery voltage action but Assigned Digital output should be high | FR 1 | GCU should not execute the High battery voltage if action is selected as none, even the battery voltage remains more than the threshold value & but assigned Digital ouput should be high. | Not tested in this build | Working as expected | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-06-11
34 | GCU_34 | Supercapacitor Monitoring
|  | a) Select the action for the low Super Capacitor. Connect the variable DC power supply to the GCU and decrease the voltage below threshold value. | Low Super Capacitor action | FR 1 | GCU should execute the warning, shut down as per the action selected for the Super Capacitor voltage. | Not tested in this build | Working as expected | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-06-11
|  | b) Set the delay for the low Super Capacitor. Decrease the Super Capacitor voltage below the threshold value and observe the time required foe GCU for generating alarm. | Low Super Capacitor voltage delay | FR 1 | GCU should execute the low Super Capacitor voltage alarm if the Super Capacitor voltage remains less than the threshold value for time period set in the delay field. | Not tested in this build | Working as expected | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-06-11
|  | c) Select the action for the low Super Capacitor & assign any one output as Super Capacitor unhealthy for the low Super Capacitor. Observe the Digital output along with the GCU to generate the alarm. | Low Super Capacitor action with Assigned output high | FR 1 | GCU should execute the low Super Capacitor if the Super Capacitor remains less than the threshold value & assigned ouput should be high. | Not tested in this build | Working as expected | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-06-11
|  | d) Select the action (None) for the Super Capacitor low & assign any one Digital output as Super Capacitor Unhealthy for the Super Capacitor low voltage. Observe the Digital output along with the GCU to generate the alarm. | should not take Low Super Capacitor voltage action but Assigned Digital output should be high | FR 1 | GCU should not execute the Low Super Capacitor voltage if action is selected as none, even the Super Capacitor voltage remains less than the threshold value & but assigned Digital ouput should be high. | Not tested in this build | Working as expected | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-06-11
|  | e)Select the action for the High Super Capacitor voltage. Increase the voltage of DC power supply above the threshold value. | High Super Capacitor voltage action | FR 1 | GCU should execute the warning, shut down as per the action selected for the High Super CApacitor voltage. | Not tested in this build | Working as expected | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-06-11
|  | f) Set the delay for the high Super Capacitor voltage. Observe the time required for the GCU to generate the alarm. | High Super Capacitor voltage delay | FR 1 | GCU should execute the high Super Capacitor voltage if the Super Capacitor voltage remains more than the threshold value for time period set in the delay field | Not tested in this build | Working as expected | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-06-11
|  | g) Select the action for the high Super Capacitor voltage & assign any one output as Super Capacitor unhealthy for the high Super Capacitor voltage. Observe the Digital output along with the GCU to generate the alarm. | High Super Capacitor voltage action with Assigned output high | FR 1 | GCU should execute the high Super Capacitor voltage if the Super Capacitor voltage remains more than the threshold value & assigned ouput should be high. | Not tested in this build | Working as expected | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-06-11
|  | h) Select the action (None) for the high Super Capacitor voltage & assign any one Digital output as Super Capacitor Unhealthy for the high Super Capacitor voltage. Observe the Digital Output along with GCU to generate the alarm. | shoul not take High Super Capacitor voltage action but Assigned Digital output should be high | FR 1 | GCU should not execute the High Super Capacitor voltage if action is selected as none, even the Super Capacitor voltage remains more than the threshold value & but assigned Digital ouput should be high. | Not tested in this build | Working as expected | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-06-11
35 | GCU_36 | Charging Alternator Monitoring
|  | a) Select the action for the charge alternator ure. Drop the voltage of the charging alternator pin by connecting it to the GND. | Charge alternator action. | FR 1 | GCU should give the warning or shut down as per the action set for the charge alternator when voltage of charging alternator pin is reduced to 0V. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-05
|  | b) Select the threshold value as 1V for the charge alternator ure voltage. Connect the charge alternator pin to the GND. | Charge alternator threshold. | FR 1 | GCU should give the warning or shut down as per the action set for the charge alternator when voltage of that particular pin is reduced to 0V ie below the threshold value. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-05
|  | c) Set the charge alternator delay time and then connect the pin to the GND. | Charge alternator Delay. | FR 1 | GCU should give the alarm only when the voltage is below the threshold value for the time greater than the Delay time. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-05
|  | d) Set threshold greater than current CA voltage i.e. 12 V and check for charge alarm |  |  | GCU should generate Charge alarm after by taking CA delay after completion of safety mon delay. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-05
|  | Test to be performed on the actual DG. Connect D+ pin to charging alternator with 1Ohm resistance in series. Connect one probe of Picoscope across 1 Ohm resistance for current measurement and another probe to D+ pin and Ground for voltage measurement. Give Crank to engine and check the waveform of voltage and current while cranking. | o | FR 1 | During cranking sequence, True RMS Power supplied to the field coil of charging alternator should be around 3 Watt. | Working as expected.Tested using Firmware R0V11.Values found at boundry level | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Upendra K | 2024-04-02
35 | GCU_35 | Preheat
|  | a) Select one digital output as a Preheat. Then set the preheat timer in the preheat timer. Start the DG and observe the LED at preheat output. | Preheat timer | FR 1 | The preheat timer field of the GUI should be enabled only when the Preheat is selected at one of the output sources. The preheat output should be high for the timer set in the preheat field before the first crank attempt.
|  | b) Select the temperature enable and temperature limit. With the help of POT, decrease the temperature below this value. Start the DG and slowly increase the temperature. | Temperature Limit. | FR 1 | Preheat output should be high as long as the temperature is less than the temperature limit value.
Test cases for modified functinality of preheat added in test case 47
36 | GCU_36 | Conatctor status LEDs
|  | Select the contactor outputs and set the polarity as energize. |  |  | GCU should indicate the status of the contactors. Genset contactor LED should glow when the “Close genset contactor” output is active. Similarly, mains contactor LED should glow when the “Close mains contactor” output is active. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-08
|  | Refer attached Contactor latching sheet |  |  |  | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Purushottam P | 2024-03-14
37 | GCU_37 | word Level for the Configuration Modes |  | FR 41
|  | Enter the config mode with Master pin |  |  | No provision to edit password by keypad | Not tested in this build | Working as expected | Not tested in this build | Not tested in this build | Pass | Rahul Hage | 2024-06-18
|  | Event log when parameter channge from config by master or user pin. |  | FR 42 | Event log should get logged after editing the parameters using Master pin and user pin. | NA | NA | NA | NA | NA | NA | NA
|  | Update only the firmware from factory flash or mobile flash and enter into config by modified words or pin. |  |  | GCU should take words or Pin stored in /cfgc after updating the firmware (change in revision version of firmware) and should not enter by modified word. | NA | NA | NA | NA | NA | NA | NA
|  | Update only the firmware from factory flash or mobile flash and check the profile |  |  | GCU should upload New Factory updated profile with same number selected by user before flashing and Current changes in profiles should get overwrite. | NA | NA | NA | NA | NA | NA | NA
38 | GCU_38 | Maintenance due alarm | Maintenance due alarm | FR 1
|  | Set the engine run hours or the date for the maintenance alarm. Observe that the alarm occurs when the date occurs or engine runs for the set number of hours. |  |  | GCU should give the maintenance alarm when the due date occurs or when the run hours are reached. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-08
39 | GCU_39 | Number of starts and Trips | Number of starts and Trips | FR 1
|  | Start and stop the engine for several times. Also, simulate the alarm conditions for several times. Check that the number of starts and trips are getting logged correctly. |  |  | GCU should count and store the number of trips and starts correctly. It should display the same on the monitoring screen as well. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-08
40 | GCU_40 | Engine, Site battery, Mains and Tampered Run hours
|  | Test to be conducted with the debugger. Attach the code to the GCU with the help of programmer and set the value of the engine run hour through it and follow the test cases. |  | FR 1 |  | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-20
|  | Set the run hours within the range 0 to 300 hours. Run the engine for the 1 minute and then switch off the GCU supply when DG is ON. |  | FR 1 | GCU should update the engine run hours after every 1 minute.It also increments No of Starts by 1. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-20
|  | Set the run hours within the range 301 to 1000 hours. Repeat the same procedure. |  | FR 1 | GCU should update the run hours after every 2 minutes. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-21
|  | Set the run hours within the range 1001 to 5000 hours. Repeat the same procedure. |  | FR 1 | GCU should update the run hours after every 5 minutes. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-21
|  | Set the run hours above the 5001 hours. Repeat the same procedure. |  |  | GCU should update the run hours after every 15 minutes. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-21
|  | Boundary Value Testing of Cumulative Counts of parameters. |  | FR 74
|  | With the help of debugger increase the Max count of 1.ENGINE RUN HOURS 2.NO. OF STARTS and NO. OF TRIPS 3.Mains and Site Battery Run hours 4. Mains and DG kWh 5.Mains and DG kVAh 6.Mains and DG kVArh and observe the rollover as well for all parameters |  |  | Incremented Max values of parameter should be displayed correctly and Parameter should be rollover to zero value after Max count of parameter. 1.ENGINE RUN HOURS : 65000 2.NO. OF STARTS and NO. OF TRIPS: 65000 3. Mains, Site Battery Run hours: 65000 4.Cummulutive counts of kWh DG/Mains: 50,00,000 5.Cummulutive counts of kVAh DG/Mains:50,00,000 6.Cummulutive counts of kVArh DG/Mains: 50,00,000 | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-22
|  | With the help of debugger increase the Max count of Load Histogram and observe the rollover as well for all parameters |  |  | Incremented Max values of parameter should be displayed correctly and Parameter should be rollover to zero value after Max count of parameter: 65535 | NA | NA | NA | NA | NA | NA | NA
41 | GCU_41 | Below 7.8V (LOW BAT) EEPROM Writing
|  | Switch ON Controller below 7.8 V, Now Go to configuration setting and make changes in configuration and save the configuration |  |  | After changing the configuration in configuration setting, Changes should reflect in controller after saving configuration in Run time but when we Power reset the controller, it should not show the configuration which was saved during low battery condition. Controller should show the configuration which was saved during healthy battery condition. | NA | NA | NA | NA | NA | NA | NA
|  | Cumulative counts of controller during battery voltage below 7.8 V |  |  | If controller running during low battery condition it should increase the following parameter count during run time, 1. KWH 2.KVaH 3.Engine Run hours 3. No of Starts 4. No of trips 5. Mains run hours. But if we power reset Controller it should not save that cumulative count which was counted during LOW battery condition. | NA | NA | NA | NA | NA | NA | NA
|  | Switch ON controller with 12 V after that start engine. Connect Load Allow controller to increase cumulative counts of KWH,KVAH,KVARH,Start, trip and mains run hours. Again make supply voltage below 7.8 V. Allow engine to run for a while. Again make supply voltage 12V and check the status of cumulative counts |  |  | If controller is switched ON with 12 V battery condition and engine is running then it should increase the following parameter count during run time, 1. kWh 2.kWAh 3.Engine Run hours 4. No of Starts 5. No of trips 6. Mains run hours. When we make battery voltage below 7.8 V in Engine running condition cumulative counts should increase and controller should save those cumulative counts if we increase the voltage level to 12 V again in engine running condition. | NA | NA | NA | NA | NA | NA | NA
|  | Switch ON controller with 12 V after that start engine. Connect Load Allow controller to increase cumulative counts of KWH,KVAH,KVARH,Start, trip and mains run hours. Again make supply voltage below 7.8 V. Allow engine to run for a while. Stop the engine. Again make supply voltage 12V and check the status of cumulative counts after Power reset |  |  | If controller is switched ON with 12 V battery condition and engine is running then it should increase the following parameter count during run time, 1. KVAH 2.KWH 3.Engine Run hours 4. No of Starts 5. No of trips 6. Mains run hours. When we make battery voltage below 7.8 V in Engine running condition cumulative counts should increase and controller should not save those cumulative counts if we power reset controller after increasing the voltage level to 12 V when engine stops. | NA | NA | NA | NA | NA | NA | NA
|  | Make controller ON during healthy battery condition, after that make battery voltage unhealthy. And power reset Controller. |  |  | If controller running during healthy battery condition it should increase the following parameters count during run time, 1. kWh 2.KVAh 3.Engine Run hours 4. No of Starts 5. No of trips 6. Mains run hours. But if we Decrease Controller voltage it should show that cumulative count which was counted during LOW battery condition. But after power reset of controller, it should show the counts which was counted during healthy battery condition | NA | NA | NA | NA | NA | NA | NA
|  | Switch ON controller below 5.8 V, Generate some event logs and reset controller |  |  | Controller should not save any event | NA | NA | NA | NA | NA | NA | NA
|  | Connect USB to controller and generate some events |  |  | Event Logs should get save in controller | NA | NA | NA | NA | NA | NA | NA
42 | GCU_42 | Fan Current monitoring
Connect the earth CT input to the GCU. Set the CT ratio for the earth leakage current CT. one of the phase through the earth CT to simulate the current flowing through neutral. Set the threshold for the leakage current and action for the leakage current.
|  | Keep fan current monitoring enable. Set Fan current high threshold and action. Observe for individual phases by switch on and off the lamps manually . | Fan Current High Threshold |  | When fan current is observed above high current threshold, Then GCU should give High fan current alarm and should take the action accordingly. | Not tested in this build | Same as expected | Not tested in this build | Not tested in this build | Pass | Sangeet Wankhede | 2024-06-19
|  | Keep fan current monitoring enable. Set Fan current low threshold and action. | Fan Current Low Threshold |  | When fan current is observed below low current threshold, Then GCU should give low fan current alarm and should take the action accordingly. | Not tested in this build | Same as expected | Not tested in this build | Not tested in this build | Pass | Sangeet Wankhede | 2024-06-19
|  |  | Current Monitoring delay |  | It should take action after set delay | Not tested in this build | Same as expected | Not tested in this build | Not tested in this build | Pass | Sangeet Wankhede | 2024-06-19
43 | GCU_43 | DG Waveform Detection
|  | Keep DG waveform detection enable through GUI.(This feature cannot be enable or disable with keypad) |  |  | Editable via keypad | NA | NA | NA | NA | NA | NA | NA
|  | Set up for testing: Connect NI automation RIG to GCU and set the time for ramp and thresholds of RPM in GUI of NI RIG. |  |  | Not tested for this build | NA | NA | NA | NA | NA | NA | NA
|  | Refer sheet ”Tamper proofing test scenario” sheet for test cases and result |  | FR 24 | Not tested for this build | NA | NA | NA | NA | NA | NA | NA
44 | GCU_44 | Site battery Run hours update
In auto mode
Test to be conducted with the debugger. Attach the code to the GCU with the help of programmer and set the value of the site batt run hour through it and follow the test cases.
|  | Set the run hours within the range 0 to 300 hours. Keep site batt healthy and Mains unhealthy in auto mode for the 1 minute and then switch off the GCU supply |  |  | GCU should update the site batt run hours after every 1 minute. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-22
|  | Set the run hours within the range 301 to 1000 hours. Keep site batt healthy and Mains unhealthy in auto mode for the 2 minutes and then switch off the GCU supply. |  | FR 1 | GCU should update the site batt run hours after every 2 minutes. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-22
|  | Set the run hours within the range 1001 to 5000 hours. Keep site batt healthy and Mains unhealthy in auto mode for the 5 minute and then switch off the GCU supply. |  | FR 1 | GCU should update the site batt run hours after every 5 minutes. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-22
|  | Set the run hours above the 5001 hours. Keep site batt healthy and Mains unhealthy in auto mode for the 15 minute and then switch off the GCU supply when DG is ON. |  | FR 1 | GCU should update the site batt run hours after every 15 minutes. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-22
|  | In Manual mode |  | FR 1
|  | Keep GCU in manual mode . Assign sources as Mains and gen contactor latched to two different inputs. Keep mains healthy and generator ON. |  |  | GCU should not increase site battery run hours if Mains contactor latched input is activated or Gen contactor latched input is activated. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-22
|  | Keep GCU in manual mode . Do not Assign sources as Mains and gen contactor latched to two different inputs. Keep mains healthy and generator ON. |  |  | GCU should not increase site battery run hours if mains contactor is latched or genset contactor is latched | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-22
|  | Refer the sheet of “Site battery run hours ” test scenario |  | FR 19
45 | GCU_45 | Night Mode Restriction |  | FR 15
Configuration: Enable: Night Mode Restriction (Through GCU or GUI) Configure Night Restriction Duration. (Through GCU or GUI)
Manual Mode:
|  | Start the DG in Manual mode just before Night Restriction timer start. |  |  | DG should take stop action as soon as Night restriction timer starts. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-08
|  | Let the Night mode Restriction timer start and try to start the DG in Manual Mode. |  |  | DG should not Start. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-08
|  | Let the Night mode Restriction timer end and try to start the DG in Manual Mode immediately. |  |  | DG should Start. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-08
Auto Mode:
|  | Start the DG in Auto by making Mains Unhealthy, just before Night Restriction timer start. |  |  | DG should take stop action as soon as Night restriction timer starts. And should latch or unlatch mains contactor depending on mains status. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-08
|  | Let the Night Restriction timer start and try to start the DG in Auto Mode. |  |  | DG should not Start. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-08
|  | Let the Night Restriction timer end and try to start the DG in Auto Mode immediately. |  |  | DG should Start. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-08
|  | Make mains unhealthy during Night restriction timer. |  |  | As Mains Detect delay and return to mains delay are already over during night restriction timer, DG should start as soon as night restriction timer ends. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-08
Mode change during Night Restriction timer
|  | Change the Mode from Auto to Manual during Night Restriction timer. |  |  | Mode change during Night restriction timer should be Allowed | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-08
|  | Change the Mode from Auto to Manual or Manual to Auto during Night Restriction timer. |  |  | Mode change during Night restriction timer should be Allowed | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-08
Mains Contactor handling During Night Restriction
|  | Make mains healthy/ unhealthy during night restriction timer. Check contactor status. |  |  | Mains contactor should be latched/unlatched accordingly status of mains only in auto mode. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-08
|  | Make mains healthy/ unhealthy during night restriction timer. Check contactor status. And Change mode from Auto to manual and then again to Auto mode |  |  | Mains contactor should be latched/unlatched accordingly status of mains only in auto mode. But when mode is changed to Auto then Mains contactor should be unlatched. And when again Mode is changed to auto then Mains contactor should get latched. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-08
|  | Let the Night Restriction timer end and try to start the DG in Auto Mode immediately. |  |  | DG should Start. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-08
|  | Keep Mains Unhealthy during Night mode Restriction and make mains Healthy during Night mode off duration. |  |  | As Mains Detect delay and return to mains delay are already done during night mode off duration, DG should start as soon as night mode off duration ends, But when Mains is detected healthy then GCU should send stop command | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-08
|  | 1. Before Night restriction timer start in Auto Mode, generate any fault condition (Electrical trip/Shutdown/ to start/ to stop) alarm and keep mains unhealthy. Now clear that alarm when night Restriction timer is running. 2. Wait till the Night restriction timer completed. |  |  | 1. Alarm should get cleared but GCU should not send start command and DG should not Start. 2. After completion of night restriction timer, GCU should take Start command in Auto Mode depending on Mains status and after alarm gets cleared. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-08
Start of Night Mode Restriction timer in Start Sequence (Timer):
|  | Make such a configuration, so that Night restriction timer should start in each of the timer of starting sequence (Auto- start delay/ crank start delay, cranking, crank rest delay, Warmup Delay, Load Transfer delay and safety monitoring). |  |  | DG should take stop as soon as Night restriction timer starts when any of the start sequence timer running. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-08
Start of Night Restriction timer in Stop Sequence (Timer):
|  | Make such a configuration, so that Night restriction timer should start in each of the timer of stop sequence (Cooling Down, Stop action, additional stop action). |  |  | DG should take continue stop as soon as Night mode restriction timer starts when any of the stop sequence timer running. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-08
|  | Start of Night Mode Restriction timer in ‘ to Start’ or ‘ to Stop’ condition. |  |  |  | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-08
|  | In Auto Mode, Let the to start condition occur, and during Night mode DG off duration clear that alarm by keeping Mains Unhealthy. |  |  | GCU should not give start command again after clearing that alarm. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-08
|  | Start the DG and let it take shutdown due to Night mode restriction start time. While taking shutdown let the ‘ to stop’ condition occur. Now clear that alarm during night mode DG off duration. |  |  | After clearing ’ to stop’ alarm, GCU should not give Start command. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-08
Date roll over condition
|  | configure the night mode in GCU in such a way that date roll over condition should occur. e.g. set DG off time as 21.00.00 and DG off duration as 04.00.00 | Date roll over condition |  | GCU should enter night mode for the set time. GCU should come out of night mode and takes the necessary action as per mains/DG/Mode status | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-08
Night Mode Restriction with BTS and Shelter SMD
|  | Keep Mains unhealthy, Site battery unhealthy and Shelter temp healthy. Allow DG to start due to unhealthy site battery. Set Night mode timing and DG OFF duration for Night Timings. |  |  | DG should start due to unhealthy Site battery. GCU should display Remaining min for DG run. GCU should take stop action if GCU reach set night mode timing and it should continue night mode till the night mode timer gets over. GCU should check all conditions (Mains status, BTS status, Shelter status) while exit from night mode and should take the action accordingly. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-08
|  | Keep Mains unhealthy, Site battery healthy and Shelter temp unhealthy. Allow DG to start due to unhealthy site battery. Set Night mode timing and DG OFF duration for Night Timings. |  |  | DG should start due to unhealthy shelter temperature. GCU should display Remaining min for DG run. GCU should take stop action if GCU reach set night mode timing and it should continue night mode till the night mode timer gets over. GCU should check all conditions (Mains status, BTS status, Shelter status) while exit from night mode and should take the action accordingly. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-08
47 | GCU_47 | Preheating SMD |  | FR 23
|  | Check Interlocking of Engine temp and Ambient Temp in preheat section |  |  | GCU should allow enabling only one of the parameter between Engine Temp and Ambient Temp in Preheat section
|  | Keep Engine OFF. Keep Engine Temp enable in preheat section and make sure that Engine temp should be greater than Engine Temp Threshold. Also ensure that there should not be any Warning, Shut-down or Electrical trip alarm. Give Start command to DG |  |  | GCU should take start action without preheat timer and preheat output should be OFF
|  | Keep Engine OFF. Enable Ambient Temp enable in preheat section. Assign Ambient Temp_SW as a source at any of the input. Input should be de-active. Also ensure that there should not be any Warning, Shut-down or Electrical trip alarm. Give Start command to DG |  |  | GCU should take start action without preheat timer and preheat output should be OFF | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-08
|  | Generate any shut-down or Electrical trip alarm. In above two cases. |  |  | GCU should give stop command and should stop the engine. | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-08
|  | Keep Engine OFF. Keep Engine Temp enable in preheat section and make sure that Engine temp should be less than Engine Temp Threshold. Also ensure that there should not be any Warning, Shut-down or Electrical trip alarm. Give Start command to DG |  |  | GCU should take start action with preheat timer and preheat output should be ON for preheat timing
|  | Keep Engine OFF. Keep Ambient Temp enable in preheat section. Assign Ambient Temp_SW as a source at any of the input. Input should be activated. Also ensure that there should not be any Warning, Shut-down or Electrical trip alarm. Give Start command to DG |  |  | GCU should take start action with preheat timer and preheat output should be ON for preheat timing
|  | Keep Engine OFF. Keep Engine Temp and Ambient Temp Disabled in Preheat section.Also ensure that there should not be any Warning, Shut-down or Electrical trip alarm. Give Start command to DG |  |  | GCU should take start action with preheat timer and preheat output should be ON for preheat timing
|  | Keep Engine OFF. Keep Engine Temp enable in preheat section. Assign Ambient Temp_SW as a source at any of the input. Input should be activated. Keep Engine Temp greater than Engine Temp Threshold. Also ensure that there should not be any Warning, Shut-down or Electrical trip alarm. Give Start command to DG |  |  | GCU should take start action without preheat timer and preheat output should be OFF | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | Pass | Sahil Sheikh | 2024-03-08
48 | GCU_48 | Re flashing by mobile flash and Factory flash
|  | Re flashing by mobile flash and Factory flash from old product revision to new product revision when there is Ram calibration (parameters) change in product revision |  |  |  | NA | NA | NA | NA | NA | NA | NA
|  | Flash the device with old product revision by factory flash capture the device info after booting the device. Now connect the device to Mobile flash application through android phone(Application should be installed on phone) Flash the desired package and boot the device and capture the device, now try to enter into the configuration mode by entering word set in CFGC. |  |  | Device info after re flashing should get as desired and device should enter into configuration mode by word mentioned in CFGC and parameters should be editable. | NA | NA | NA | NA | NA | NA | NA
|  | Flash the device with old product revision by factory flash capture the device info after booting the device. Now connect the device to Factory Flash Flash the desired (Updated) package and boot the device and capture the device, now try to enter into the configuration mode by entering word set in CFGC. |  |  | Device info after re flashing should get as desired and device should enter into configuration mode by word mentioned in CFGC and parameters should be editable. | NA | NA | NA | NA | NA | NA | NA
|  | change the master and user Pin and Reflashing or updating only firmware |  | FR 14 | Device info after re flashing should get as desired and device should not enter into configuration mode by modified master or user pin instead it should enter into config by CFGC word and parameters should be editable CFGC word | NA | NA | NA | NA | NA | NA | NA
|  | change the master and user Pin and Modifying only CGFZ (write config file from GUI) |  |  | Device info after reflashing should get as desired only CFGz checksum should change and device should enter into configuration mode by modified master and user word and parameters should be editable by modified word. | NA | NA | NA | NA | NA | NA | NA
49 | GCU_49 | Profile selection |  | FR 28
|  | Enter into config mode by profile selection Password- Master Password PIN1. |  |  | Profile selection menu should be visible under MISC menu and profile should be scroll up and down by GCU Facia UP-DOWN key. | Not Testede in this Build | Not Testede in this Build | Not Testede in this Build | As Expected | Pass | Rahul Hage | 2024-06-24
|  | Enter into config mode by user word PIN2. |  |  | Profile can not be modify | Not Testede in this Build | Not Testede in this Build | Not Testede in this Build | As Expected | Pass | Rahul Hage | 2024-06-24
|  | 1.Select the profile , change the configuration save the settings 2.change the profile. 3. again go to the config and select the previously selected profile in which configuration is modified. |  | FR 46 | The changes done in the profile should not be saved after selecting of another profile, config changes are only on current profile and should not affect factory flashed profile. | Not Testede in this Build | Not Testede in this Build | Not Testede in this Build | Not Testede in this Build | NA | NA | NA
51 | GCU_51 | DG Idle Run Logic
Select the communication mode as a MODBUS from the configuration menu. Check its functionality by connecting the RS485 cable to the GCU And ensure the DG load less than 0.2kW
|  | Select the communication mode as a MODBUS. | MODBUS connectivity | FR 40 | The parameters and registers should display the values and the bits as show in the MODBUS sheet. | NA | NA | NA | NA | NA | NA | NA
|  | Start DG , Do not put load on DG and check the register map for the alarms as per the table (In Solid state O/P bit number 3) | DG running in DG contactor unlatched | FR 40 | GCU should send High on the MODBUS when DG idle run condition is present. GCU should make DG idle run bit high after expiry of time delay ( either safety Mon or warm up which ever it is higher) plus hard coded delay of 5 sec in DG contactor in unlatched condition. | NA | NA | NA | NA | NA | NA | NA
|  | Start DG and Keep the load is zero when DG is running, However controller triggered contactor ON command | DG running in DG contactor latched | FR 40 | GCU should make DG idle run bit High when genset is running at no load condition or the load on genset is below 0.2 kW. After expiry of time delay ( either safty mon or warm up which ever it is higher) plus hard coded delay of 5 sec. | NA | NA | NA | NA | NA | NA | NA
|  | Generate the " to Stop condition" and check DG idle run bit on Modbus | To Stop condition | FR 40 | GCU should send High on the MODBUS when " to Stop" alarm is present and DG running at no load or less than 0.2 Kw. GCU should send High on MODBUS When " to stop" alarm is clear but actual " to Stop" condition is available. | NA | NA | NA | NA | NA | NA | NA
|  | Start the DG in Manual/Auto mode and put the load more than 0.2kW | DG Idle Run bit low | FR 40 | GCU should send Low on the MODBUS when DG idle run condition is not present as load is more than 0.2kW and contactor latched | NA | NA | NA | NA | NA | NA | NA
|  | Start the DG in Manual/Auto mode and put the load less than 0.2kW. Assign the any DIG IN as an User confugured. Select the polarity for the activation and action as Electrical trip and apply input. | During Cooling Down |  | When input is activated, GCU should stop the engine with taking cooling down time, in cooling down time GCU should send DG idle run bit "Low" on the MODBUS | NA | NA | NA | NA | NA | NA | NA
|  | Start the DG in Manual/Auto mode and check DG idel Run bit with starting timers | Warm up and Safety monitoring delay | FR 40 | GCU should not send "High" on the MODBUS till Warm up and Safety monitoring timer is expires (whichever is higher ). | NA | NA | NA | NA | NA | NA | NA
52 | GCU_52 | Password access
|  | Refer word access sheet for word access of parameters by Master PIN and USER PIN | Password access | FR 41, FR 50 | GCU should have parameter access editing by Master PIN and USER PIN as per sheet no.11 | Not Testede in this Build | Not Testede in this Build | Not Testede in this Build | Not Testede in this Build | NA | NA | NA
53 | GCU_53 | Interlocking between Sensors: |  |  |  | Not Testede in this Build | Not Testede in this Build | Not Testede in this Build | Not Testede in this Build | NA | NA | NA
|  | Interlocking between Analog Input 1 & Aux S3 Sensor |  |  |  | Not Testede in this Build | Not Testede in this Build | Not Testede in this Build | Not Testede in this Build | NA | NA | NA
|  | 1. Set Analog input 1 as a 'LOP' and try to select S3 sensor as a 'LOP 4-20mA' (from GCU) |  |  | whenAnalog input 1 is selected as a LOP then S3 sensor selection drop down menu should not display LOP 4-20/ 0-5 | Not Testede in this Build | Not Testede in this Build | Not Testede in this Build | Not Testede in this Build | NA | NA | NA
|  | 2. Set S3 sensor as a 'LOP-Current 4-20mA' and try to select Analog input 1 as a 'LOP' |  |  | when S3 sensor selected as a 'LOP 04-20mA', Analog input 1 should not display LOP in drop down menu | Not Testede in this Build | Not Testede in this Build | Not Testede in this Build | Not Testede in this Build | NA | NA | NA
|  | 3. Set S3 sensor as a 'LOP 0-5V' and try to select Analog input 1 as a 'LOP' |  |  | when S3 sensor selected as a 'LOP 0-5V', Analog input 1 should not display LOP in drop down menu | Not Testede in this Build | Not Testede in this Build | Not Testede in this Build | Not Testede in this Build | NA | NA | NA
54 | GCU_54 | Interlocking of Open circuit Action:
|  | Select following sensor from GCU one by one and check it Open circuit actions: 1. Select Aux S3 sensor as a 'LOP 4-20mA' |  |  | Open circuit action should be settable to 'Warning' & 'Shutdown' | Not Testede in this Build | Not Testede in this Build | Not Testede in this Build | Not Testede in this Build | NA | NA | NA
|  | Select following sensor from GCU and check it Open circuit actions: 1. Select Aux S3 sensor as a 'LOP 0-5V' |  |  | Open circuit action should be settable to 'None', 'Warning' & 'Shutdown' | Not Testede in this Build | Not Testede in this Build | Not Testede in this Build | Not Testede in this Build | NA | NA | NA
|  | Select following sensor from GCU and check it Open circuit actions: 1. Select Aux S4 sensor as a 'FUEL 0-5V' |  |  | Open circuit action should be settable to 'None', 'Warning' & 'Shutdown' | Not Testede in this Build | Not Testede in this Build | Not Testede in this Build | Not Testede in this Build | NA | NA | NA
|  | Select LOP 0-5V sensor from S3 with circuit fault action 'None' and then select 4-20mA sensor from S3 |  |  | when LOP 4-20mA sensor is selected from S3 sensor, circuit fault action should be displayed either 'Warning' or 'Shutdown' | Not Testede in this Build | Not Testede in this Build | Not Testede in this Build | Not Testede in this Build | NA | NA | NA
|  | Select any sensor from S3 and change its sensor to other in drop down menu and check |  |  | When select other sensor, GCU should load default values (SD, Warning, Calib table) of selected sensor. | Not Testede in this Build | Not Testede in this Build | Not Testede in this Build | Not Testede in this Build | NA | NA | NA
ID Serial Number Read Write
Enter in Configuration by Entering Pin 1 and Enter in ID menu> Serial Number Data
Edit Genset Serial No, Engine Sr No, Alternator Sr No, Eng Controller Sr No, Site ID or Edit this by Tool
Controller Serial number will not be editable by Keypad. It should be eited by Tolol Only
Exit configuration and verify the data written in Serial number is matching with modbus register for INDUS map
55 | GCU_55 | Automatic mode switching
In manual mode:
Enable the mode switching, start the DG in manual mode
|  | Summary | Coverage in Value(number) | Coverage in %
|  | No of test cases | 708
|  | No of test cases performed | 666 | 94.0678
|  | No. of test cases ed | 333 | 47.0339
|  | No of tesr cases ed | 333 | 47.0339
|  | No of test cases not tested | 42 | 5.9322

## VI measurements
SEDEMAC | Test Report For : SW-GC2X-GC2115-RA6M2 | [6 empty] | Doc # | SW-TEST_GC2X-GC2115-RA6M2
[8 empty] | Rev #/ Rev Date | 0.27/21 June 2024
[8 empty] | Page # | 2 of 24
CT ratio=100/5
| APPLIED through OMICRON |  |  | APPLIED through OMICRON |  |  | CT correction Factor | Observed on GCU |  |  | Observed on GCU |  |  | Actual result Firmware R0V07 | Actual result Firmware R0V23 | Actual result Firmware R0V25 | Actual result Firmware R0V27 | PASS / FAIL | Tested by | Date of testing
| VR | VY | VB | IR | IY | IB | 1.07 | VR | VY | VB | IR | IY | IB | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | PASS | Upendra K | 2024-03-04
| 190 | 190 | 190 | 0.090A | 0.090A | 0.09A | 1.07 | 189 | 190 | 190 | 1.9 | 1.9 | 1.9 | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | PASS | Upendra K | 2024-03-04
| 230 | 230 | 230 | 1 | 1 | 1 | 1.07 | 229 | 229 | 229 | 21.3 | 21.2 | 21.4 | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | PASS | Upendra K | 2024-03-04
| 250 | 250 | 250 | 1.235 | 1.235 | 1.235 | 1.07 | 249 | 249 | 249 | 26.2 | 26.2 | 26.4 | Working as expected | Not tested in this build | Not tested in this build | Not tested in this build | PASS | Upendra K | 2024-03-04
NOTE

## EGR-ECU Code Protocol
SEDEMAC |  | Test Report For : SW-GC2X-GC2115-RA6M2 | [7 empty] | Doc # | SW-TEST_GC2X-GC2115-RA6M2
[10 empty] | Rev #/ Rev Date | 0.27/21 June 2024
[10 empty] | Page # | 3 of 24
Test Procedure:
Configure Any Digital Input as "EGR Input", Configure Any Output as "Inducement Buzzer " and connect one buzzer /hooter at the output terminal
Using Omicron setup apply following type of Pulses one by one to "EGR Input" pin .For corresponding Error Code Pattern "Fault" string should get displayed on GCU screen
While engine is in "OFF ready state" when any of the following pulse is applied then GCU should not display any fault.
Engine is In GCU EGR Error detection works while Engine is ON .
Open following file in Omicron & generate each type of pulse one by one to simulate the faults
| Omicron EGR pulses file link | https://sedemac.sharepoint.com/:u:/s/ProductLineGCU-GCUandB12ProductDevelopment/EfauwSylSIxEhD-vsYLe1soBUweo3cWsMfEy_bKEePghzg?e=LEZ90N
| NOTE: | Implementation of MODBUS to be verified and tested in seperate MODBUS sheet
[8 empty] | Expected Result (EGR Fault code string) | Actual results | Pass/Fail | Tested by | Date of testing | R2V10
[8 empty] | <No Fault> | Working as expected | Pass | Purushottam P | 2024-04-02 | ok
[8 empty] | ECU FAULTY | Working as expected | Pass | Purushottam P | 2024-04-02 | ok
[8 empty] | Tmp Sen Open | Working as expected | Pass | Purushottam P | 2024-04-02 | ok
[8 empty] | Tmp Sen Flty | Working as expected | Pass | Purushottam P | 2024-04-02
[8 empty] | EGR VLV Open | Working as expected | Pass | Purushottam P | 2024-04-02
[8 empty] | EGR Vlv Flty | Working as expected | Pass | Purushottam P | 2024-04-02
[8 empty] | EGR Not Lift | Working as expected | Pass | Purushottam P | 2024-04-02
[8 empty] | EGR Not Clse | Working as expected | Pass | Purushottam P | 2024-04-02
Sr. No. | Test Case ID | Description |  |  |  | Module/ Functionality under test | Corresponding SRS ID | Expected Result (EGR Fault code string) | Actual results | Pass/Fail | Tested by | Date of testing
|  | After powering ON GCU should display"<No Fault>" |  |  |  | EGR MON screen |  | After powering ON GCU should display"<No Fault>" | Working as expected | Pass | Purushottam P | 2024-04-02
|  | If any fault (1 to 8 from above table) is simulated during "Engine OFF Ready " state then GCU should not display any fault .It should display"<No Fault>" constantly | [5 empty] | If any fault (1 to 8 from above table) is simulated during "Engine OFF Ready " state then GCU should not display any fault .It should display"<No Fault>" constantly | Working as expected | Pass | Purushottam P | 2024-04-02
|  | WHen STOP key is pressed while Engine is in OFF state then it should clear ALarm screen fault eg."EGR Fault" ,It should also make Status EGR MON screen as "<No Fault>" | [5 empty] | WHen STOP key is pressed while Engine is in OFF state then it should clear ALarm screen fault eg."EGR Fault" ,It should also make Status EGR MON screen as "<No Fault>" | Working as expected | Pass | Purushottam P | 2024-04-02
|  | IF EGR In is not selected then GCU shoul should not display separate EGR MON screen on main screens section | [5 empty] | IF EGR In is not selected then GCU shoul should not display separate EGR MON screen on main screens section | Working as expected | Pass | Purushottam P | 2024-04-02
|  | WHen Engine run for more 72Hrs with fault then it should take shutdown and event log gets saved for this event. | [5 empty] | WHen Engine run for more 72Hrs with fault then it should take shutdown and event log gets saved for this event. | Working as expected | Pass | Purushottam P | 2024-04-02
|  | WHen Engine starts & run under Healthy state continuously without detecting any fault then it should not increase heal time unless it detects any fault (at least once) . |  |  |  | EGR MON screen |  | WHen Engine starts & run under Healthy state continuously without detecting any fault then it should not increase heal time unless it detects any fault (at least once). Fault detection count & FAULT TIMER value will be considered in next Engine ON cycle.Same for Heal Timer also | Working as expected | Pass | Sangeet Wankhede | 2024-06-18
|  | In above case (while engine running condition only)after fault recovery heal timer continues for 40 Hrs then it resets both Fault Timer & Heal Timer to zero and same (italic bold) steps repeted while engine is running condition. | [5 empty] | In above case (while engine running condition only)after fault recovery heal timer continues for 2 min then it resets both Fault Timer & Heal Timer to zero and same (italic bold) steps repeted while engine is running condition in upcoming Engine ON/OFF cycles | Working as expected | Pass | Purushottam P | 2024-04-02
|  | Apply 4th pulse "Tmp Sen Flty" then engine should take immediate shutdown after providing Fourth pulse. |  |  |  | EGR MON screen & EVENT LOG |  | GCU should take immediate shutdown after providing Fourth pulse to EGR IN input .For this fault "EGR Fault Shutdown"should be logged under event log. | Working as expected | Pass | Purushottam P | 2024-04-02
|  | When NO EGR_IN is selected at Input then it should not show EGR MON screen. |  |  |  | EGR MON screen |  |  | Not Testede in this Build | NA | NA | NA
|  | When EGR_IN is selected but input pin kept open |  |  |  | EGR MON screen |  | It shoudl show EGR ECU Healthy constantly on screen while engine ON and engien is OFF | Working as expected | Pass | Purushottam P | 2024-04-02
| CAN | For COP Demonstration need to transmit EGR Inducement Fault Hrs and Heal Time on below CAN ID(J1939) |  | Expected Result (EGR Fault code string) | Actual results (R0V23) | PASS/FAIL | Tested by | Date of testing
|  | 1. Inducement Buzzer Output will be Trigger base on EGR Fault Time |  | NA | Working as expected | Pass | Sangeet Wankhede | 2024-06-18
|  | i. After 36 Hrs Low level Inducement (Only Warning Action) will be Trigger and Inducement Buzzer will activated 2 Sec ON and 5 Sec OFF |  | NA | Working as expected | Pass | Sangeet Wankhede | 2024-06-18
|  | ii. After 72 Hrs High level Inducement will be Trigger and Inducement Buzzer will activated 2 Sec ON and 2 Sec OFF. And Engine will be Shutdown. |  | NA | Working as expected | Pass | Sangeet Wankhede | 2024-06-18
|  | iii. On Acknowledgment GCU should deactivate the Inducement Buzzer and Clear Alarm from GCU Display. |  | NA | Not Testede in this Build | NA | NA | NA
|  | iv. During next start Engine will take Action as per current EGR input status. |  | NA | Not Testede in this Build | NA | NA | NA
|  | v. Inducement hooter will be active only if EGR fault is present. during heal time it will not trigger. |  | NA | Not Testede in this Build | NA | NA | NA
EGR MOITORING DISPLAY SCREENS FOR reference
|  | SR # | EGR Input Pulse | GCU Display Result
|  | 1 | ECU Healthy/Every Signal OK | <No Fault>
|  | 2 | ECU Faulty or NO Supply | EGR Faulty
|  | 3 | Temp sensor is open or faulty | Tmp Sen Open
|  | 4 | Temp sensor keep it out In Ambient Temp | Tmp Sen Flty
|  | 5 | Valve wire open | EGR Vlv Open
|  | 6 | Valve Sensor not connected of faulty | EGR Vlv Flty
|  | 7 | Valve Not Lifting | EGR Not Lift
|  | 8 | Valve Not Closing | EGR Not Clse

## MODBUS Parameters(Rjio)
SEDEMAC |  | Test Report For :SW-GC2X-GC2115-RA6M2 | [5 empty] | Doc # | SW-TEST_REPORT-GC2X-GC2115-RA6M2
[8 empty] | Rev #/ Rev Date | 0.27/21 June 2024
[8 empty] | Page # | 4 of 24
| NOTE | ADDITIONAL REGISTERS ASSIGNED FOR INDICATION OF FOLLOWING PARAMETERS TO BE ADDED AND TESTED IN R0V27
| Parameter | Name | Registers assigned
| 8 New Digital Outputs | Digital OUTPUT I | To be confirmed from customer & add here
Digital OUTPUT J
Digital OUTPUT K
Digital OUTPUT L
Digital OUTPUT M
Digital OUTPUT N
Digital OUTPUT O
Digital OUTPUT P
Parameter Details | Data type | Decimal Address | Reg Offset | Measuring Unit | Scale Factor/Bits/Sign | MODBUS Actual Results | GCU screen Actual Results | PASS/FAIL | Tested By | Date
Digital Alarm 1 | int | 16384 | 0x4000 | - | Refer Table 35
Digital Alarm 2 | int | 16385 | 0x4001 | - | Refer Table 35
Solid-state O/P | int | 16386 | 0x4002 | - | Refer Table 35
Mains Phase 1 Volt | int | 16387 | 0x4003 | V | 1 | 239 | 239 | Pass | Purushottam P | 2024-03-06
Mains Phase 2 Volt | int | 16388 | 0x4004 | V | 1 | 243 | 244 | Pass | Purushottam P | 2024-03-06
Mains Phase 3 Volt | int | 16389 | 0x4005 | V | 1 | 238 | 238 | Pass | Purushottam P | 2024-03-06
DG Phase 1 Volt | int | 16390 | 0x4006 | V | 1 | 238 | 238 | Pass | Purushottam P | 2024-03-06
DG Phase 2 Volt | int | 16391 | 0x4007 | V | 1 | 244 | 244 | Pass | Purushottam P | 2024-03-06
DG Phase 3 Volt | int | 16392 | 0x4008 | V | 1 | 239 | 239 | Pass | Purushottam P | 2024-03-06
Load Current Phase 1 | int | 16393 | 0x4009 | A | 1 | 7 | 7.2 | Pass | Purushottam P | 2024-03-06
Load Current Phase 2 | int | 16394 | 0x400A | A | 1 | 7 | 7.6 | Pass | Purushottam P | 2024-03-06
Load Current Phase 3 | int | 16395 | 0x400B | A | 1 | 7 | 7.1 | Pass | Purushottam P | 2024-03-06
Mains kWh (long) | int | 16396 | 0x400C | kWh | 1/bit0 to bit15 | 12 | 12.8 | Pass | Purushottam P | 2024-03-06
| int | 16397 | 0x400D | kWh | 1/bit16 to bit31 | 0 | -- | -- | -- | --
DG kWh (long) | int | 16398 | 0x400E | kWh | 1/bit0 to bit15 | 8 | 8.8 | Pass | Purushottam P | 2024-03-06
| int | 16399 | 0x400F | kWh | 1/bit16 to bit31 | 0 | --- | -- | -- | --
DG Run Hour | int | 16400 | 0x4010 | Hrs | 1/Hours | 2 | 2 | Pass | Purushottam P | 2024-03-06
| int | 16401 | 0x4011 | Mins | 1/Minutes | 6 | 6 | Pass | Purushottam P | 2024-03-06
Mains Run Hour | int | 16402 | 0x4012 | Hrs | 1/Hours | 0 | 0 | Pass | Purushottam P | 2024-03-06
| int | 16403 | 0x4013 | Mins | 1/Minutes | 47 | 47 | Pass | Purushottam P | 2024-03-06
DG Battery Voltage | int | 16404 | 0x4014 | V | 0.1 | 99 | 9.9 | Pass | Purushottam P | 2024-03-06
Site Battery Voltage | int | 16405 | 0x4015 | V | 0.1 | 499 | 49.9 | Pass | Purushottam P | 2024-03-06
Fuel in litres | int | 16406 | 0x4016 | Ltrs | 1 | 22 | 22 | Pass | Purushottam P | 2024-03-06
Mains R kW | int | 16407 | 0x4017 | kW | 0.1 | 16 | 1.7 | Pass | Purushottam P | 2024-03-06
Mains Y kW | int | 16408 | 0x4018 | kW | 0.1 | 18 | 1.8 | Pass | Purushottam P | 2024-03-06
Mains B kW | int | 16409 | 0x4019 | kW | 0.1 | 16 | 1.7 | Pass | Purushottam P | 2024-03-06
DG R kW | int | 16410 | 0x401A | kW | 0.1 | 17 | 1.7 | Pass | Purushottam P | 2024-03-06
DG Y kW | int | 16411 | 0x401B | kW | 0.1 | 18 | 1.8 | Pass | Purushottam P | 2024-03-06
DG B kW | Int | 16412 | 0x401C | kW | 0.1 | 16 | 1.6 | Pass | Purushottam P | 2024-03-06
Site Run Hours | Int | 16413 | 0x401D | Hrs | 1 | 99 | 99 | Pass | Purushottam P | 2024-06-24
| Int | 16414 | 0x401E | Mins | 1 | 50 | 50 | Pass | Purushottam P | 2024-06-24
TMPR Run Hours | Int | 16415 | 0x401F | Hrs | 1 | 99 | 99 | Pass | Purushottam P | 2024-06-24
| Int | 16416 | 0x4020 | Mins | 1 | 1 | 1 | Pass | Purushottam P | 2024-06-24
TMPR kWh (Long) | Int | 16417 | 0x4021 | kWh | 1/Bit 0 to Bit 15 | 2100 | 2100 | Pass | Purushottam P | 2024-06-24
| Int | 16418 | 0x4022 | kWh | 1/Bit 16 to Bit 31 | 0 | 0 | Pass | Purushottam P | 2024-06-24
EB MCCB Status | Int | 16419 | 0X4023 | NA | 1/Bit0 | 1 | EB MCCB feedback ON | Pass | Purushottam P | 2024-06-24
DG MCCB Status | Int |  |  |  | 1/Bit1 | 1 | DG MCCB feedback ON | Pass | Purushottam P | 2024-06-24
ECU Healthy/Every Signal OK | Int | 16420 | 0X4024 | NA | 1/Bit0 | 1 | <No Fault> | Pass | Sangeet Wankhede | 2024-06-18
ECU Faulty or NO Supply | Int |  |  | NA | 1/Bit1 | 1 | ECU FAULTY | Pass | Sangeet Wankhede | 2024-06-18
Temperature Sensor is open or faulty. | Int |  |  | NA | 1/Bit2 | 1 | Tmp Sen Open | Pass | Sangeet Wankhede | 2024-06-18
Temperature Sensor Keep in Ambient Temperature | Int |  |  | NA | 1/Bit3 | 1 | Tmp Sen Flty | Pass | Sangeet Wankhede | 2024-06-18
EGR Valve Wire Open | Int |  |  | NA | 1/Bit4 | 1 | EGR VLV Open | Pass | Sangeet Wankhede | 2024-06-18
EGR Valve Sensor not connected or faulty | Int |  |  | NA | 1/Bit5 | 1 | EGR Vlv Flty | Pass | Sangeet Wankhede | 2024-06-18
EGR Valve Not Lifting / EGR valve is short. | Int |  |  | NA | 1/Bit6 | 1 | EGR Not Lift | Pass | Sangeet Wankhede | 2024-06-18
EGR Valve Not Closing | Int |  |  | NA | 1/Bit7 | 1 | EGR Not Clse | Pass | Sangeet Wankhede | 2024-06-18
EGR Fault time | Int | 16421 | 0X4025 | Minute | 1 | 1 | Egr fault time | Pass | Sangeet Wankhede | 2024-06-18
EGR Heal Time | Int | 16422 | 0X4026 | Minute | 1 | 1 | Egr Heal time | Pass | Sangeet Wankhede | 2024-06-18
Bit 0-3 (All EGR Fault Notificaiton/Warning and EGR strategy shutdown after 72Hrs after EGR Fault) | Int | 16423 | 0X4027 | *Bit 0-3 as 0000 - No Shutdown 0001 - EGR Fault Notification 0010 - Low Level Warning 0011 – Shutdown due to EGR fault . * *Bit 4-15 as Reserved (0000) | Bit 0-3 | 1 | Notification | Pass | Sangeet Wankhede | 2024-06-18
[6 empty] | 1 | warning | Pass | Sangeet Wankhede | 2024-06-18
[6 empty] | 1 | shutdown | Pass | Sangeet Wankhede | 2024-06-18
Engine Coolant Temperature | Int | 16432 | 0x4030 | Deg C | 1 | 125 | 125 | Pass | Purushottam P | 2024-06-18
Engine Oil Pressure | Int | 16433 | 0x4031 | Bar | 0.1 | 49 | 50 | Pass | Purushottam P | 2024-06-18
Engine Speed | Int | 16434 | 0x4032 | RPM | 1 | 1500 | 1500 | Pass | Purushottam P | 2024-06-18
DG R freq | Int | 16435 | 0x4033 | Hz | 0.1 | 500 | 50 | Pass | Purushottam P | 2024-06-18
DG Y freq | Int | 16436 | 0x4034 | Hz | 0.1 | 499 | Seprate Freq not availabe on screen | Pass | Purushottam P | 2024-03-06
DG B freq | Int | 16437 | 0x4035 | Hz | 0.1 | 499 | Seprate Freq not availabe on screen | Pass | Purushottam P | 2024-03-06
DG Apparent Power R kVA | Int | 16438 | 0x4036 | kVA | 0.1 | 16 | 1.7 | Pass | Purushottam P | 2024-03-06
DG Apparent Power Y kVA | Int | 16439 | 0x4037 | kVA | 0.1 | 18 | 1.8 | Pass | Purushottam P | 2024-03-06
DG Apparent Power B kVA | Int | 16440 | 0x4038 | kVA | 0.1 | 16 | 1.7 | Pass | Purushottam P | 2024-03-06
DG Reactive Power R KVAr | Int | 16441 | 0x4039 | KVAr | 0.1 | 1 | 0.1 | Pass | Purushottam P | 2024-03-06
DG Reactive Power Y KVAr | Int | 16442 | 0x403A | KVAr | 0.1 | 1 | 0.2 | Pass | Purushottam P | 2024-03-06
DG Reactive Power B KVAr | Int | 16443 | 0x403B | KVAr | 0.1 | 1 | 0.1 | Pass | Purushottam P | 2024-03-06
DG kVAh (long) | Int | 16444 | 0x403C | kVAh | 1 | 9 | 9.2 | Pass | Purushottam P | 2024-03-06
| Int | 16445 | 0x403D | kVAh | 1 | 0 | -- | Pass | Purushottam P | 2024-03-06
DG kVArh (long) | Int | 16446 | 0x403E | kVArh | 1/bit0 to bit15 | 0 | 0.7 | Pass | Purushottam P | 2024-03-06
| Int | 16447 | 0x403F | kVArh | 1/bit16 to bit31 | 0 | -- | Pass | Purushottam P | 2024-03-06
DG Power Factor R | Int | 16448 | 0x4040 | - | 0.01 | 99 | 0.99 | Pass | Purushottam P | 2024-03-06
DG Power Factor Y | Int | 16449 | 0x4041 | - | 0.01 | 99 | 0.99 | Pass | Purushottam P | 2024-03-06
DG Power Factor B | int | 16450 | 0x4042 | - | 0.01 | 99 | 0.99 | Pass | Purushottam P | 2024-03-06
DG Average Power Factor | int | 16451 | 0x4043 | - | 0.01 | 99 | 0.99 | Pass | Purushottam P | 2024-03-06
Fuel Percentage | int | 16452 | 0X4044 | - | 0.1 | 221 | 22 | Pass | Purushottam P | 2024-03-06
SPN1 | Unsigned Int | 16453 | 0x4045 (MSB 16 Bit) | NA | 1 | Not tested in this build | Not tested in this build | NA | NA | NA
|  | 16454 | 0x4046 (LSB 16 Bit) | NA | 1 | Not tested in this build | Not tested in this build | NA | NA | NA
FMI1 | Unsigned Int | 16455 | 0x4047 | NA | 1 | Not tested in this build | Not tested in this build | NA | NA | NA
SPN2 | Unsigned Int | 16456 | 0x4048 (MSB 16 Bit) | NA | 1 | Not tested in this build | Not tested in this build | NA | NA | NA
|  | 16457 | 0x4049 (LSB 16 Bit) | NA | 1 | Not tested in this build | Not tested in this build | NA | NA | NA
FMI2 | Unsigned Int | 16458 | 0x404A | NA | 1 | Not tested in this build | Not tested in this build | NA | NA | NA
SPN3 | Unsigned Int | 16459 | 0x404B (MSB 16 Bit) | NA | 1 | Not tested in this build | Not tested in this build | NA | NA | NA
|  | 16460 | 0x404C (LSB 16 Bit) | NA | 1 | Not tested in this build | Not tested in this build | NA | NA | NA
FMI3 |  | 16461 | 0x404D | NA | 1 | Not tested in this build | Not tested in this build | NA | NA | NA
Refer Table 35 |  |  |  | MODBUS Actual Results | GCU screen Actual Results | REMARKS | Tested By | Date
Bits | Digital Alarm 1 | Digital Alarm 2 | Solid State O/P
Bit0 | Canopy Door Open /User configured DIG H | Mains Contactor Feedback IN | Output8 (H) | 1,1,1 | Auxiliary input H | Pass | Purushottam P | 2024-03-07
Bit1 | Smoke Fire | Overload | Output7 (G) | 1,1,1 | Smoke fire, Overload | Pass | Purushottam P | 2024-03-07
Bit2 | LOP Switch/Sensor | Mains Fail | Output6 (F) | 1, | Low oil pressure (switch) / Low oil pressure (sensor), mains failed | Pass | Purushottam P | 2024-03-07
Bit3 | HCT Switch/Sensor | Reserved | Output5 (E) | 1, | High eng temp (switch) , High temp semsor pending. | NA | NA | NA
Bit4 | DG Contactor On | DG Fail To Start | Output4 (D) | 1,1 ,1 | Fail to start | Pass | Purushottam P | 2024-03-07
Bit5 | V Belt Fail | Reserved | Output3 (C) | 1,1,1 | NA | Pass | Purushottam P | 2024-03-07
Bit6 | Half Fuel /User Configured DIG IN F | Over Speed | Output2 (B) | 1,1,1 | Half fuel,Over speed, Fail to start | Pass | Purushottam P | 2024-03-07
Bit7 | Low Fuel Sensor/Switch | Under Speed | Output1 (A) |  | Low fuel level (sensor)/ Low fuel level (switch), underspeed, Preheating | Pass | Purushottam P | 2024-03-07
Bit8 | Emergency Stop | DG On | Reserved | 1,1,1 | Emergency stop | Pass | Purushottam P | 2024-03-07
Bit9 | Auto/Manual Mode | Reserved | Reserved | 1,1 ,1 | 1-Manual,0-Auto. | Pass | Purushottam P | 2024-03-07
Bit10 | Reserved | Remote Start/stop | DG Contactor Relay | 1,1 ,1 | -- | Pass | Purushottam P | 2024-03-07
Bit11 | Reserved | High Canopy Temp / (User config/AUX DIG IN-G) | Mains Contactor Relay | 1,1 ,1 | -- | Pass | Purushottam P | 2024-03-07
Bit12 | Reserved | Main Alternator Fault | Reserved | NA | NA | NA | NA | NA
Bit13 | Low Water Level | Reserved | Reserved | 1,1 ,1 | Low water level switch | Pass | Purushottam P | 2024-03-07
Bit14 | Super Capacitor Fail | Battery Charger Fail / DIG Input B / any input (Keep Mains Healthy,DG OFF & apply input) | Reserved | 1,1 ,1 | Battery charger fail | Pass | Purushottam P | 2024-03-07
Bit15 | Reserved | Reserved | Reserved | NA | NA | NA | NA | NA

## Modbus (INDUS)
SEDEMAC |  | Test Report For :SW-GC2X-GC2115-RA6M2 | [5 empty] | Doc # | SW-TEST_REPORT-GC2X-GC2115-RA6M2
[8 empty] | Rev #/ Rev Date | 0.27/21 June 2024
[8 empty] | Page # | 5 of 24
Controller: | ECON-MAN-IND
Firmware | v2.04
Protocol | Modbus RTU (RS485)
Sn. | Parameters | Units of | Data Type | Size in byte | Conversion | Type of Register | Modbus | Modbus Register | No. of | Remarks | R0V17 | R0V20 | R0V23 | R0V24 | Pass/Fail | Tested by | Date of testing
|  | Measurement | (Float/Hex etc.) |  | Multiplier to read the data |  | Register Address | Actual Implemented in Procom Controller | Registers required |  | Modbus Result | Modbus Result | Modbus Result | Modbus Result
INPUT REGISTER (FC 04)
1 | Product Type (CPCB4 Generator - 20) | NA | Unsigned Integer | 2 | 1 | Input Register | 1 | 0 | 1 | 20->CPCB4 | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
2 | Product Make | NA | Unsigned Integer | 2 | 1 | Input Register | 2 | 1 | 1 | 100->TMTL 110->M&M 0->Procom | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
3 | Generator Phase (1 for Single Phase 3 for Three Phase) | NA | Unsigned Integer | 2 | 1 | Input Register | 3 | 2 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
4 | Fuel Type (Diesel -1 , Gas-2) | NA | Unsigned Integer | 2 | 1 | Input Register | 4 | 3 | 1 | 1->Diesel | PAss | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
5 | Product Rating (Please mention the exact rating) | NA | Unsigned Long Integer | 4 | 0.1 | Input Register | 5 & 6 | 4 & 5 | 2 | Rating in KVA | NOT tested in this build | NOT tested in this build | Pass | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-14
6 | SOFTWARE/FIRMWAREVERSION (Partner Specific) | Version | Unsigned Integer | 2 | 0.01 | Input Register | 7 | 6 | 1 |  | NOT tested in this build | NOT tested in this build | Pass | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-14
7 | PROTOCOLVERSION (Indus Priority) - 23 | Version | Unsigned Integer | 2 | 1 | Input Register | 8 | 7 | 1 |  | NOT tested in this build | NOT tested in this build | Pass | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-14
8 | Genset Serial No | NA | ASCII String | 20 | NA | Input Register | 2018-09-01 | 8-17 | 10 | Max 19 characters (null-terminated) (Reserved for now) | NOT tested in this build | NOT tested in this build | Pass | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-14
9 | Engine Serial No | NA | ASCII String | 20 | NA | Input Register | 19-28 | 18-27 | 10 | Max 19 characters (null-terminated) (Reserved for now) | NOT tested in this build | NOT tested in this build | Pass | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-14
10 | Alternator Serial No | NA | ASCII String | 20 | NA | Input Register | 29-38 | 28-37 | 10 | Max 19 characters (null-terminated) (Reserved for now) | NOT tested in this build | NOT tested in this build | Pass | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-14
11 | Main Controller Serial No | NA | ASCII String | 20 | NA | Input Register | 40-49 | 39-48 | 10 | Max 19 characters (null-terminated) (Reserved for now) | NOT tested in this build | NOT tested in this build | Pass | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-14
12 | Engine Controller Serial No | NA | ASCII String | 20 | NA | Input Register | 50-59 | 49-58 | 10 | Max 19 characters (null-terminated) (Reserved for now) | NOT tested in this build | NOT tested in this build | Pass | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-14
13 | SITE ID | NA | ASCII String | 10 | NA | Input Register | 60-64 | 59-63 | 5 | Max 19 characters (null-terminated). But only the first 9 characters are shown if it's length exceeds 9 character. (Reserved for now) | NOT tested in this build | NOT tested in this build | Pass | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-14
14 | DATE | Date | Unsigned Integer | 2 | 1 | Input Register | 65 | 64 | 1 | Current Date | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
15 | HOUR | Hour | Unsigned Integer | 2 | 1 | Input Register | 66 | 65 | 1 | Current Hour | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
16 | MINUTES | Minutes | Unsigned Integer | 2 | 1 | Input Register | 67 | 66 | 1 | Current Minutes | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
17 | SECONDS | Seconds | Unsigned Integer | 2 | 1 | Input Register | 68 | 67 | 1 | Current Seconds | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
18 | MONTH | Month | Unsigned Integer | 2 | 1 | Input Register | 69 | 68 | 1 | Current Month | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
19 | YEAR | Year | Unsigned Integer | 2 | 1 | Input Register | 70 | 69 | 1 | Current Year | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
20 | Generator R Phase Voltage | Volt | Unsigned Integer | 2 | 0.01 | Input Register | 71 | 70 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
21 | Generator Y Phase Voltage | Volt | Unsigned Integer | 2 | 0.01 | Input Register | 72 | 71 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
22 | Generator B Phase Voltage | Volt | Unsigned Integer | 2 | 0.01 | Input Register | 73 | 72 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
23 | Generator Line Voltage RY | Volt | Unsigned Integer | 2 | 0.01 | Input Register | 74 | 73 | 1 |  | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
24 | Generator Line Voltage YB | Volt | Unsigned Integer | 2 | 0.01 | Input Register | 75 | 74 | 1 |  | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
25 | Generator Line Voltage BR | Volt | Unsigned Integer | 2 | 0.01 | Input Register | 76 | 75 | 1 |  | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
26 | Generator Frequency | Hz | Unsigned Integer | 2 | 0.01 | Input Register | 77 | 76 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
27 | N-E (Neutral to Earth) Voltage | Volt | Unsigned Integer | 2 | 0.01 | Input Register | 78 | 77 | 1 | Always 0 (Not populated) | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
28 | Load Current R Phase | Amps | Unsigned Integer | 2 | 0.01 | Input Register | 79 | 78 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
29 | Load Current Y Phase | Amps | Unsigned Integer | 2 | 0.01 | Input Register | 80 | 79 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
30 | Load Current B Phase | Amps | Unsigned Integer | 2 | 0.01 | Input Register | 81 | 80 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
31 | Total Load Current | Amps | Unsigned Integer | 2 | 0.01 | Input Register | 82 | 81 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
32 | R Phase Power Factor | PF | Unsigned Integer | 2 | 0.01 | Input Register | 83 | 82 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
33 | Y Phase Power Factor | PF | Unsigned Integer | 2 | 0.01 | Input Register | 84 | 83 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
34 | B Phase Power Factor | PF | Unsigned Integer | 2 | 0.01 | Input Register | 85 | 84 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
35 | Engine Speed (RPM) | RPM | Unsigned Long Integer | 4 | 1 | Input Register | 86- 87 | 85-86 | 2 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
36 | Generator Total Run Hours | Hour | Unsigned Long Integer | 4 | 0.1 | Input Register | 88- 89 | 87-88 | 2 | Doesn't include Tamper run hours | NOT tested in this build | NOT tested in this build | Pass | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-14
37 | Generator Remote Run Hours | Hour | Unsigned Long Integer | 4 | 0.1 | Input Register | 90- 91 | 89-90 | 2 | Doesn't include Tamper run hours | NOT tested in this build | NOT tested in this build | Pass | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-14
38 | Generator Manual Run Hours | Hour | Unsigned Long Integer | 4 | 0.1 | Input Register | 92- 93 | 91-92 | 2 | Doesn't include Tamper run hours | NOT tested in this build | NOT tested in this build | Pass | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-14
39 | Generator No Load Run Hours | Hour | Unsigned Long Integer | 4 | 0.1 | Input Register | 94- 95 | 93-94 | 2 | Doesn't include Tamper run hours | NOT tested in this build | NOT tested in this build | Pass | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-14
40 | Generator ON Load Run Hours | Hour | Unsigned Long Integer | 4 | 0.1 | Input Register | 96-97 | 95-96 | 2 | Doesn't include Tamper run hours | NOT tested in this build | NOT tested in this build | Pass | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-14
41 | Generator Output Power - Real | KW | Unsigned Integer | 2 | 0.01 | Input Register | 98 | 97 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
42 | Generator Output Power - Apparent | KVA | Unsigned Integer | 2 | 0.01 | Input Register | 99 | 98 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
43 | Generator Output Power - Reactive | KVAR | Unsigned Integer | 2 | 0.01 | Input Register | 100 | 99 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
44 | Total Generator Energy | KWH | Unsigned Long Integer | 4 | 0.01 | Input Register | 101-102 | 100-101 | 2 | Doesn't include Tamper KWh | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
45 | Canopy Temperature (above Engine) | Degree C | Unsigned Integer | 2 | 0.1 | Input Register | 103 | 102 | 1 | Always 0xffff (Not populated) | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
46 | Canopy Temperature (far end side from Radiator) | Degree C | Unsigned Integer | 2 | 0.1 | Input Register | 104 | 103 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
47 | Air Inlet Temperature | Degree C | Unsigned Integer | 2 | 0.1 | Input Register | 105 | 104 | 1 | Always 0xffff (Not populated) | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
48 | Fuel Temperature | Degree C | Unsigned Integer | 2 | 0.1 | Input Register | 106 | 105 | 1 | Always 0xffff (Not populated) | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
49 | Exhaust Temperature | Degree C | Unsigned Long Integer | 4 | 0.1 | Input Register | 107-108 | 106-107 | 2 | Always 0xffffffff (Not populated) | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
50 | Catalyst Converter Temperature | Degree C | Unsigned | 4 | 0.1 | Input Register | 109-110 | 108-109 | 2 | Always 0xffffffff (Not populated) | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
51 | Engine Coolant Temp | Degree C | Unsigned Long Integer | 4 | 0.1 | Input Register | 111-112 | 110-111 | 2 | 0xffffffff when Sensor Open or if sensor is disabled | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
52 | Radiator Coolant Temp - inlet | Degree C | Unsigned Long Integer | 4 | 0.1 | Input Register | 113-114 | 112-113 | 2 | Always 0xffffffff (Not populated) | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
53 | Radiator Coolant Temp - outlet | Degree C | Unsigned Long Integer | 4 | 0.1 | Input Register | 115-116 | 114-116 | 2 | Always 0xffffffff (Not populated) | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
54 | Stop Solenoid Body Temperature | Degree C | Unsigned Long Integer | 4 | 0.1 | Input Register | 117-118 | 116-117 | 2 | Always 0xffffffff (Not populated) | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
55 | LLOP (Low Lube oil pressure) | psi | Unsigned Integer | 2 | 0.01 | Input Register | 119 | 118 | 1 | 0xffff when Sensor Open or if sensor is disabled This is LOP | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
56 | Generator Battery Voltage | Volt | Unsigned Integer | 2 | 0.01 | Input Register | 120 | 119 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
57 | Fuel Level % | % | Unsigned Integer | 2 | 0.01 | Input Register | 121 | 120 | 1 | 0xffffffff when Sensor Open or if sensor id disabled | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
58 | Fuel Consumed in liter | Liter | Unsigned Long Integer | 4 | 0.01 | Input Register | 122-123 | 121-121 | 2 | Always 0xffffffff (Not populated) | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
59 | Gas Consumed in SCM | SCM | Unsigned Long Integer | 4 | 0.01 | Input Register | 124-125 | 123-124 | 2 | Always 0xffffffff (Not populated) | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
60 | Total no of Cranks | Nos | Unsigned Long Integer | 4 | 0.01 | Input Register | 126-127 | 125-126 | 2 |  | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
61 | No of Cranks failed attempt | Nos | Unsigned Long Integer | 4 | 0.01 | Input Register | 128-129 | 127-128 | 2 |  | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
62 | Air Inlet Pressure | mBar | Unsigned Integer | 2 | 0.01 | Input Register | 130 | 129 | 1 | Always 0xffff (Not populated) | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
63 | Engine Oil Level % | % | Unsigned Integer | 2 | 0.01 | Input Register | 131 | 130 | 1 | Always 0xffff (Not populated) | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
64 | Turbo Oil Pressure | mBar | Unsigned Integer | 2 | 0.01 | Input Register | 132 | 131 | 1 | Always 0xffff (Not populated) | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
65 | Engine Coolant Level % | % | Unsigned Integer | 2 | 0.01 | Input Register | 133 | 132 | 1 | Always 0xffff (Not populated) | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
66 | Pilot Regulator input Pressure | mBar | Unsigned Integer | 2 | 0.01 | Input Register | 134 | 133 | 1 | Always 0xffff (Not populated) | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
67 | Pilot Regulator output Pressure | mBar | Unsigned Integer | 2 | 0.01 | Input Register | 135 | 134 | 1 | Always 0xffff (Not populated) | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
68 | Engine (Gas or Diesel) (For Diesel- 1 and Gas- 2) | NA | Unsigned Integer | 2 | 1 | Input Register | 136 | 135 | 1 | 1->Diesel | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
69 | DG Vibration Sensor output in kHz or Volt |  | Unsigned Integer | 2 | 0.01 | Input Register | 137 | 136 | 1 | Always 0xffff (Not populated) | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
70 | Radiator Water Level | % | Unsigned Integer | 2 | 0.01 | Input Register | 138 | 137 | 1 | Always 0xffff (Not populated) | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
71 | NTP Factor Auto Calculation | Nos | Unsigned Integer | 2 | 0.01 | Input Register | 139 | 138 | 1 | Always 0xffff (Not populated) | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
72 | AVR Excitation Voltage | Volt | Unsigned Integer | 2 | 0.01 | Input Register | 140 | 139 | 1 | Always 0xffff (Not populated) | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
73 | Lube Oil Viscosity | mm2/S | Unsigned Integer | 2 | 0.01 | Input Register | 141 | 140 | 1 | Always 0xffff (Not populated) | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
74 | Started on Remote mode or Manual | NA | Unsigned Integer | 2 | 1 | Input Register | 142 | 141 | 1 | 0->Manual Mode 1->Remote Mode | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
| Mode (Remoe Mode-1,Manual Mode- 0) | [9 empty] | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
75 | DG On Trigger due to Battery Volt. or Shelter Temp. (Battery - 1, temp-2) | NA | Unsigned Integer | 2 | 1 | Input Register | 143 | 142 | 1 | Always 0xffff (Not populated) | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
76 | Reserved |  |  | 4 |  | Input Register | 144 | 143 | 2 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
77 | Reserved |  |  | 4 |  | Input Register | 146 | 145 | 2 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
78 | Reserved |  |  | 4 |  | Input Register | 148 | 147 | 2 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
79 | Reserved |  |  | 4 |  | Input Register | 150 | 149 | 2 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
80 | Reserved |  |  | 4 |  | Input Register | 152 | 151 | 2 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
81 | Reserved |  |  | 2 |  | Input Register | 154 | 153 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
82 | Reserved |  |  | 2 |  | Input Register | 155 | 154 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
83 | Reserved |  |  | 2 |  | Input Register | 156 | 155 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
84 | Reserved |  |  | 4 |  | Input Register | 157-158 | 156-157 | 2 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
85 | Reserved |  |  | 4 |  | Input Register | 159-160 | 158-159 | 2 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
86 | Reserved |  |  | 4 |  | Input Register | 161-162 | 160-161 | 2 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
87 | NCD Error Hrs | Hour | Unsigned Long Integer | 4 | 0.1 | Input Register | 163-164 | 162-163 | 2 |  | NOT tested in this build | NOT tested in this build | Pass | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-14
88 | NCD Heal Hrs | Hour | Unsigned Long Integer | 4 | 0.1 | Input Register | 165-166 | 164-165 | 2 |  | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Pass | Sangeet Wankhede | 2024-06-20
INPUT STATUS (FC 02)
1 | Fire/Smoke | NA | BIT | NA | NA | Input Status | 1 | 0 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
2 | Canopy Door Open | NA | BIT | NA | NA | Input Status | 2 | 1 | 1 |  | NOT tested in this build | NOT tested in this build | Pass | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-14
3 | Load on Generator | NA | BIT | NA | NA | Input Status | 3 | 2 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
4 | Generator Fail to Start | NA | BIT | NA | NA | Input Status | 4 | 3 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
5 | Generator Fail to Stop | NA | BIT | NA | NA | Input Status | 5 | 4 | 1 |  | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
6 | Generator Common Fault | NA | BIT | NA | NA | Input Status | 6 | 5 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
7 | Generator LLOP Fault | NA | BIT | NA | NA | Input Status | 7 | 6 | 1 |  | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
8 | Alternator Fault | NA | BIT | NA | NA | Input Status | 8 | 7 | 1 | Always 0 (Not populated) | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
9 | Low Fuel Level @ 15% | NA | BIT | NA | NA | Input Status | 9 | 8 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
10 | Canopy Temp High | NA | BIT | NA | NA | Input Status | 10 | 9 | 1 |  | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
11 | Engine Coolant Temperature High | NA | BIT | NA | NA | Input Status | 11 | 10 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
12 | Fuel Temperature High | NA | BIT | NA | NA | Input Status | 12 | 11 | 1 | Always 0 (Not populated) | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
13 | Exhaust Temperature High | NA | BIT | NA | NA | Input Status | 13 | 12 | 1 | Always 0 (Not populated) | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
14 | Catalyst Converter Temperature High | NA | BIT | NA | NA | Input Status | 14 | 13 | 1 | Always 0 (Not populated) | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
15 | DG IDLE RUN | NA | BIT | NA | NA | Input Status | 15 | 14 | 1 |  | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
16 | DG Overload | NA | BIT | NA | NA | Input Status | 16 | 15 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
17 | DG Battery Low | NA | BIT | NA | NA | Input Status | 17 | 16 | 1 |  | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
18 | Water in fuel alarm | NA | BIT | NA | NA | Input Status | 18 | 17 | 1 | Always 0 (Not populated) | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
19 | Water seepage alarm | NA | BIT | NA | NA | Input Status | 19 | 18 | 1 | Always 0 (Not populated) | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
20 | HT Ignition Coil open alarm | NA | BIT | NA | NA | Input Status | 20 | 19 | 1 | Always 0 (Not populated) | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
21 | Spark plug Faulty alarm | NA | BIT | NA | NA | Input Status | 21 | 20 | 1 | Always 0 (Not populated) | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
22 | Air filter choke alarm | NA | BIT | NA | NA | Input Status | 22 | 21 | 1 | Always 0 (Not populated) | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
23 | Gas Filter Choke Alarm | NA | BIT | NA | NA | Input Status | 23 | 22 | 1 | Always 0 (Not populated) | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
24 | Engine Coolant Level Low | NA | BIT | NA | NA | Input Status | 24 | 23 | 1 | Always 0 (Not populated) | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
25 | Gas Leakage Alarm | NA | BIT | NA | NA | Input Status | 25 | 24 | 1 | Always 0 (Not populated) | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
26 | System Shutdown due to Gas leakage | NA | BIT | NA | NA | Input Status | 26 | 25 | 1 | Always 0 (Not populated) | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
27 | Inginition Coil Lead disconnection alarm | NA | BIT | NA | NA | Input Status | 27 | 26 | 1 | Always 0 (Not populated) | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
28 | Generator Maintenance Alarm 50Hrs | NA | BIT | NA | NA | Input Status | 28 | 27 | 1 |  | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
29 | Generator Maintenance Alarm 100Hrs | NA | BIT | NA | NA | Input Status | 29 | 28 | 1 |  | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
30 | Generator Maintenance Alarm 500Hrs | NA | BIT | NA | NA | Input Status | 30 | 29 | 1 |  | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
31 | Generator Maintenance Alarm 1000Hrs | NA | BIT | NA | NA | Input Status | 31 | 30 | 1 |  | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
32 | Generator Maintenance Alarm 2000Hrs | NA | BIT | NA | NA | Input Status | 32 | 31 | 1 |  | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
33 | Low gas pressure at Pilot Regulator output alarm | NA | BIT | NA | NA | Input Status | 33 | 32 | 1 | Always 0 (Not populated) | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
34 | High gas pressure at Pilot Regulator output alarm | NA | BIT | NA | NA | Input Status | 34 | 33 | 1 | Always 0 (Not populated) | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
35 | Vibration sensor ON | NA | BIT | NA | NA | Input Status | 35 | 34 | 1 | Always 0 (Not populated) | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
36 | Radiator Water Level Low | NA | BIT | NA | NA | Input Status | 36 | 35 | 1 | Always 0 (Not populated) | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
37 | Engine Controller Fail alarm | NA | BIT | NA | NA | Input Status | 37 | 36 | 1 | Always 0 (Not populated) | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
38 | Main Controller Fail alarm | NA | BIT | NA | NA | Input Status | 38 | 37 | 1 |  | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
39 | AVR fail alarm | NA | BIT | NA | NA | Input Status | 39 | 38 | 1 | Always 0 (Not populated) | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
40 | PFC Board Fail alarm | NA | BIT | NA | NA | Input Status | 40 | 39 | 1 | Always 0 (Not populated) | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
41 | AVR Excitation Voltage High | NA | BIT | NA | NA | Input Status | 41 | 40 | 1 | Always 0 (Not populated) | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
42 | Over Speed alarm | NA | BIT | NA | NA | Input Status | 42 | 41 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
43 | Fuel Meter sensing high Consumption than CPH | NA | BIT | NA | NA | Input Status | 43 | 42 | 1 | Always 0 (Not populated) | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
44 | Fuel meter Tamper | NA | BIT | NA | NA | Input Status | 44 | 43 | 1 | Always 0 (Not populated) | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
45 | LLOP Tamper | NA | BIT | NA | NA | Input Status | 45 | 44 | 1 | Always 0 (Not populated) | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
46 | DG Run but no vibration alarm | NA | BIT | NA | NA | Input Status | 46 | 45 | 1 | Always 0 (Not populated) | NOT tested in this build | Pass | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
47 | Reserved | NA | BIT | NA | NA | Input Status | 47 | 46 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
48 | EGR Warning | NA | BIT | NA | NA | Input Status | 48 | 47 | 1 |  | NOT tested in this build | NOT tested in this build | Pass | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-14
49 | EGR Fault | NA | BIT | NA | NA | Input Status | 49 | 48 | 1 |  | NOT tested in this build | NOT tested in this build | Pass | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-14
50 | NCD Warning | NA | BIT | NA | NA | Input Status | 50 | 49 | 1 |  | NOT tested in this build | NOT tested in this build | Pass | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-14
51 | NCD Fault | NA | BIT | NA | NA | Input Status | 51 | 50 | 1 |  | NOT tested in this build | NOT tested in this build | Pass | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-14
52 | EGR ECU Unhealthy | NA | BIT | NA | NA | Input Status | 52 | 51 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
53 | EGR Temperature Sensor Open Warning | NA | BIT | NA | NA | Input Status | 53 | 52 | 1 |  | NOT tested in this build | NOT tested in this build | Pass | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-14
54 | EGR Temperature Sensor Faulty Warning | NA | BIT | NA | NA | Input Status | 54 | 53 | 1 |  | NOT tested in this build | NOT tested in this build | Pass | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-14
55 | EGR Valve Open Warning | NA | BIT | NA | NA | Input Status | 55 | 54 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
56 | EGR Valve Sensor Faulty Warning | NA | BIT | NA | NA | Input Status | 56 | 55 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
57 | EGR Valve Not Lifting Warning | NA | BIT | NA | NA | Input Status | 57 | 56 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
58 | EGR Valve Not Closing Warning | NA | BIT | NA | NA | Input Status | 58 | 57 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
COIL STATUS (FC 01)
1 | DG STOP Command / DG OFF | NA | BIT | NA | NA | Coil Status | 1 | 0 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
2 | DG START Command / DG ON | NA | BIT | NA | NA | Coil Status | 2 | 1 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
3 | Remote Mode | NA | BIT | NA | NA | Coil Status | 3 | 2 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
4 | Manual Mode | NA | BIT | NA | NA | Coil Status | 4 | 3 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
5 | Future Use | NA | BIT | NA | NA | Coil Status | 5 | 4 | 1 |  | NOT tested in this build | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
6 | Future Use | NA | BIT | NA | NA | Coil Status | 6 | 5 | 1 |  | NOT tested in this build | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
7 | Future Use | NA | BIT | NA | NA | Coil Status | 7 | 6 | 1 |  | NOT tested in this build | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
8 | Future Use | NA | BIT | NA | NA | Coil Status | 8 | 7 | 1 |  | NOT tested in this build | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
9 | Future Use | NA | BIT | NA | NA | Coil Status | 9 | 8 | 1 |  | NOT tested in this build | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
HOLDING REGISTER (FC 03)
1 | DG OP Voltage Low cutoff | Volt | Unsigned Integer | 2 | 1 | Holding Register | 1 | 0 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
2 | DG OP Voltage High cutoff | Volt | Unsigned Integer | 2 | 1 | Holding Register | 2 | 1 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
3 | DG start first crank set | Seconds | Unsigned Integer | 2 | 1 | Holding Register | 3 | 2 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
4 | DG start second crank set | Seconds | Unsigned Integer | 2 | 1 | Holding Register | 4 | 3 | 1 | Always 0xffff (Unused) | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
5 | DG start third crank set | Seconds | Unsigned Integer | 2 | 1 | Holding Register | 5 | 4 | 1 | Always 0xffff (Unused) | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
6 | Rest after first Crank | Seconds | Unsigned Integer | 2 | 1 | Holding Register | 6 | 5 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
7 | Rest after second Crank | Seconds | Unsigned Integer | 2 | 1 | Holding Register | 7 | 6 | 1 | Always 0xffff (Unused) | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04
8 | DG Overload Trip | Seconds | Unsigned Integer | 2 | 1 | Holding Register | 8 | 7 | 1 |  | Pass | NOT tested in this build | NOT tested in this build | NOT tested in this build | Pass | Sangeet Wankhede | 2024-06-04

## Measurements from ECU (hidden)
SEDEMAC |  | Test Report For : SW-GC2X-GC2115-RA6M2 |  |  |  | Doc # | SW-TEST_GC2X-GC2115-RA6M2
[6 empty] | Rev #/ Rev Date | 00/ 30-Sept-2021
[6 empty] | Page # | 2 of 12
This section covers testing for Measurements received from ECU
Procedure/Configuration
GO to "Engine>ENgine Type> select any engine type(Non COnventioal)
Select /Enable following sensors or /measurements from ECU'
1 | Lube Oil Pressure
| Enable Lube oil pressure sensor from ECU.set the warning and shut down threshold for the LOP. Simulate the low oil pressure level by varying values sent from ECU connected to the CAN. | LOP warning and Threshold. | FR 1 | When the LOP level is below the warning threshold, GCU should give the warning for the Low Oil Pressure. When the Lop level becomes less than the shut down threshold, GCU should generate the shut down for the Low Oil Pressure.
| Enable the pressure monitoring before crank. | High oil pressure detected | FR 1 | GCU should give high oil pressure detected warning & should not start the Genset. When condition gets cleared then the warining should be auto cleared.
| Set circuit fault action and simulate the all one by one set condition using CAN. |  |  |  | TBD
\
2 | Engine COolant Temperature
Enable The parameter of Coolant Temp from ECU
| Set the high temperature Action None/Notification/Warning/Electrical Trip/Shutdown one by one .Also set the high Temperature threshold. Simulate the high temperature warning and shutdown alarm using the CAN . | Engine Temperature Action and threshold | FR 1 | GCU should generate the alarm and should take the action as per the configured high temp action when the temperature becomes higher than the threshold value.
| Set circuit fault action and simulate the all one by one set condition using CAN. |  |  |  | TBD

## OLDFirmware ranges&dropdownList
SEDEMAC |  | Test Report For :SW-GC2X-GC2115-RA6M2 | [8 empty] | Doc # | SW-TEST_REPORT-GC2X-GC2115-RA6M2
[11 empty] | Rev #/ Rev Date | 0.27/21 June 2024
[11 empty] | Page # | 6 of 24
| MODULE | SubMenu | Parameter Name | Min | Max | Default value | Options | Data Type | Units | Pass/Failed | Tested By | Date | Strings | General | DIG Input A | Auxiliary Input A |  |  | string20
Module
General
|  |  | Profile Name |  |  | Profile 1 |  | uint8 | NA | Pass | Sahil Sheikh | 2024-03-19 |  |  | DIG Input B | Auxiliary Input B |  |  | string20
|  |  | Power On Mode |  |  | 0 | 0 - Manual 1 - Auto | uint8 | NA | Pass | Sahil Sheikh | 2024-03-19 |  |  | DIG Input C | Auxiliary Input C |  |  | string20
|  |  | Power On Lamp Test | Disable | Enable | 0 | 0-Disable 1- Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-19 |  |  | DIG Input D | Auxiliary Input D |  |  | string20
|  |  | Password Lock | NA | NA | 0 | 0-Disable 1- Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-19 |  |  | DIG Input E | Auxiliary Input E |  |  | string20
Display
|  |  | Display Contrast | 0 | 100 | 50 |  | uint8 | % | Pass | Sahil Sheikh | 2024-03-19 |  |  | DIG Input F | Auxiliary Input F |  |  | string20
|  |  | Power Save Mode | Disable | Enable | 0 | 0-Disable 1- Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-19 |  |  | DIG Input G | Auxiliary Input G |  |  | string20
|  | Modbus Communication | Comm Mode |  |  | 0 | 0 – None 1 – MODBUS | uint8 | NA | [5 empty] | DIG Input H | Auxiliary Input H |  |  | string20
|  |  | MODBUS Slave ID | 1 | 247 | 2 |  | uint8 | NA | Pass | Sahil Sheikh | 2024-03-19 |  |  | DIG Input I | Auxiliary Input I |  |  | string20
|  |  | MODBUS Baudrate |  |  | 3 | 0 – 1200 1 – 2400 2 – 4800 3 – 9600 4 – 19200 5 – 38400 6 – 57600 7– 115200 | uint8 | NA | Pass | Sahil Sheikh | 2024-03-19 |  |  | DIG Input J | Auxiliary Input J |  |  | string20
|  |  | Parity Bit |  |  | 0 | 0 – None 1 – Even 2 – Odd | uint8 | NA | Pass | Sahil Sheikh | 2024-03-19 |  |  | DIG Input K | Auxiliary Input K |  |  | string20
|  | BTS | Battery Montoring | NO | YES | 1 | 0-No 1-Yes | uint8 | NA | Pass | Sahil Sheikh | 2024-03-19 |  |  | DIG Input L | Auxiliary Input L |  |  | string20
|  |  | Low Battery Threshold | 40 | 55 | 46.5 |  | float | volt | Pass | Sahil Sheikh | 2024-03-19 |  |  | DIG Input M | Auxiliary Input M |  |  | string20
|  |  | Low Battery Monitoring Delay | 5 | 300 | 10 |  | uint16 | sec | Pass | Sahil Sheikh | 2024-03-19 |  |  | DIG Input N | Auxiliary Input N |  |  | string20
|  |  | Genset Run Duration | 1 | 720 | 270 |  | uint16 | min | Pass | Sahil Sheikh | 2024-03-19 |  |  | DIG Input O | Auxiliary Input O |  |  | string20
|  | Cyclic Mode | Cyclic Mode | NO | YES | 0 | 0-No 1-Yes | uint8 | NA | Pass | Sahil Sheikh | 2024-03-19 |  |  | DIG Input P | Auxiliary Input P |  |  | string20
|  |  | Genset Off Time | 1 | 720 | 240 |  | uint16 | min | Pass | Sahil Sheikh | 2024-03-19 |  |  | Sensor S1 Name | S1 Sensor |  |  | string20
|  |  | Genset On Time | 1 | 720 | 240 |  | uint16 | min | Pass | Sahil Sheikh | 2024-03-19 |  |  | Sensor S2 Name | S2 Sensor |  |  | string20
|  | Night Mode | Night Mode | Disable | Enable | 0 | 0-No 1-Yes | uint8 | NA | Pass | Sahil Sheikh | 2024-03-19 |  |  | Sensor S3 Name | S3 Sensor |  |  | string20
|  |  | Start Time | 0 | 23:59 | 9:59 |  | uint16 | hrs. | Pass | Sahil Sheikh | 2024-03-19 |  |  | Sensor S4 Name | S4 Sensor |  |  | string20
|  |  | Off Duration | 1 | 1440 | 480 |  | uint16 | min | Pass | Sahil Sheikh | 2024-03-19 |  |  | Profile Name | profile 1 |  |  | string20
|  | AUTO MD SWITCH | AUTO MD SWITCH | Disable | Enable | 0 | 0-Disable 1- Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-19
|  |  | MANUAL MODE TIME (Min) | 16 | 120 | 16 |  | uint16 | min | Pass | Sahil Sheikh | 2024-03-19
|  |  | OUTPUT ON TIME (Min) | 5 | 15 | 15 |  | uint8 | min | Pass | Sahil Sheikh | 2024-03-19 |  | Output Souces | Disable, |  | Engine Types | CONVENTIONAL, |  | For Yes/No and Enable/Disable | 2000-01-01
Digital Inputs
Digital Input A
|  |  | Source |  |  | 0 | 0-Not Used 1-User Configured 2-Low Fuel LVL Switch 3-Low Lube Oil Press Switch 4-High Engine Temp Switch 5-Low Water LVL Switch 6-Emergency Stop 7-Remote Start / Stop 8-Simulate Start 9-Simulate Stop 10-Simulate Auto 11-Close Gen/Open Mains Switch 12-Close Mains/Open Gen Switch 13-Simulate Mains 14-V-Belt Broken Switch 15-Mains Contactor Latched 16-Genset Contactor Latched 17-Battery Charger Fail 18-Smoke Fire 19-Mode Select Switch 20-Ambient Temp. Switch 21-EGR Digital In 22-EB MCCB On Feedback 23-DG MCCB On Feedback 24-Supercapacitor Fail | uint8 | NA | Pass | Sahil Sheikh | 2024-03-19 |  |  | Sounder Alarm, |  |  | HA2,
|  |  | Polarity |  |  | 0 | 0 – Close to activate 1 – Open to activate | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | Battery Over Volt, |  |  | R,
|  |  | Action |  |  | 0 | 0 – None 1 – Warning 2 – Electrical trip 3 – Shutdown 4 – Notification | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | Battery Under Volt, |  |  | SL90.,
|  |  | Activation |  |  | 2 | 0 – Never 1 – From Engine start 2 – From monitoring On 3 – Always | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | Charge Alt Shutdown, |  |  | R550,
|  |  | Activation Delay (Sec) | 1 | 180 | 1 |  | uint8 | sec | Pass | Sahil Sheikh | 2024-03-20 |  |  | Charge Alt Warning, |  |  | DV8,
Digital Input B
|  | Note: After 20- Ambient Temp. switch (EGR Switch) is added & After 22-DG MCCB on Feedback | Source |  |  | 0 | 0-Not Used 1-User Configured 2-Low Fuel LVL Switch 3-Low Lube Oil Press Switch 4-High Engine Temp Switch 5-Low Water LVL Switch 6-Emergency Stop 7-Remote Start / Stop 8-Simulate Start 9-Simulate Stop 10-Simulate Auto 11-Close Gen/Open Mains Switch 12-Close Mains/Open Gen Switch 13-Simulate Mains 14-V-Belt Broken Switch 15-Mains Contactor Latched 16-Genset Contactor Latched 17-Battery Charger Fail 18-Smoke Fire 19-Mode Select Switch 20-Ambient Temp. Switch 21-EGR Digital In 22-EB MCCB On Feedback 23-DG MCCB On Feedback 24-Supercapacitor Fail | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | Close Gen Contactor, |  |  | HA2_CPCB4,
|  |  | Polarity |  |  | 0 | 0 – Close to activate 1 – Open to activate | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | Close Mains Contactor, |  |  | R_CPCB4,
|  |  | Action |  |  | 0 | 0 – None 1 – Warning 2 – Electrical trip 3 – Shutdown 4 – Notification | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | Mains ure, |  |  | SL90_CPCB4,
|  |  | Activation |  |  | 2 | 0 – Never 1 – From Engine start 2 – From monitoring On 3 – Always | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | Common Alarm, |  |  | R550_CPCB4,
|  |  | Activation Delay (Sec) | 1 | 180 | 1 |  | uint8 | sec | Pass | Sahil Sheikh | 2024-03-20 |  |  | Common Electric Trip, |  |  | DV8_CPCB4,
Digital Input C
|  |  | Source |  |  | 0 | 0-Not Used 1-User Configured 2-Low Fuel LVL Switch 3-Low Lube Oil Press Switch 4-High Engine Temp Switch 5-Low Water LVL Switch 6-Emergency Stop 7-Remote Start / Stop 8-Simulate Start 9-Simulate Stop 10-Simulate Auto 11-Close Gen/Open Mains Switch 12-Close Mains/Open Gen Switch 13-Simulate Mains 14-V-Belt Broken Switch 15-Mains Contactor Latched 16-Genset Contactor Latched 17-Battery Charger Fail 18-Smoke Fire 19-Mode Select Switch 20-Ambient Temp. Switch 21-EGR Digital In 22-EB MCCB On Feedback 23-DG MCCB On Feedback 24-Supercapacitor Fail | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | Common Shutdown, |  |  | ECU_1(CS162),
|  |  | Polarity |  |  | 0 | 0 – Close to activate 1 – Open to activate | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | Common Warning, |  |  | ECU_2(CC878)
|  |  | Action |  |  | 0 | 0 – None 1 – Warning 2 – Electrical trip 3 – Shutdown 4 – Notification | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | Cooling Down,
|  |  | Activation |  |  | 2 | 0 – Never 1 – From Engine start 2 – From monitoring On 3 – Always | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | Dig In A,
|  |  | Activation Delay (Sec) | 1 | 180 | 1 |  | uint8 | sec | Pass | Sahil Sheikh | 2024-03-20 |  |  | Dig In B, |  | Input Sources | Not Used,
Digital Input D
|  |  | Source |  |  | 0 | 0-Not Used 1-User Configured 2-Low Fuel LVL Switch 3-Low Lube Oil Press Switch 4-High Engine Temp Switch 5-Low Water LVL Switch 6-Emergency Stop 7-Remote Start / Stop 8-Simulate Start 9-Simulate Stop 10-Simulate Auto 11-Close Gen/Open Mains Switch 12-Close Mains/Open Gen Switch 13-Simulate Mains 14-V-Belt Broken Switch 15-Mains Contactor Latched 16-Genset Contactor Latched 17-Battery Charger Fail 18-Smoke Fire 19-Mode Select Switch 20-Ambient Temp. Switch 21-EGR Digital In 22-EB MCCB On Feedback 23-DG MCCB On Feedback 24-Supercapacitor Fail | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | Dig In C, |  |  | User Configured,
|  |  | Polarity |  |  | 0 | 0 – Close to activate 1 – Open to activate | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | Dig In D, |  |  | Low Fuel LVL Switch
|  |  | Action |  |  | 0 | 0 – None 1 – Warning 2 – Electrical trip 3 – Shutdown 4 – Notification | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | Dig In E, |  |  | Low Lube Oil Press Switch
|  |  | Activation |  |  | 2 | 0 – Never 1 – From Engine start 2 – From monitoring On 3 – Always | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | Dig In F, |  |  | High Engine Temp Switch,
|  |  | Activation Delay (Sec) | 1 | 180 | 1 |  | uint8 | sec | Pass | Sahil Sheikh | 2024-03-20 |  |  | Dig In G , |  |  | Low Water LVL Switch,
Digital Input E
|  |  | Source |  |  | 0 | 0-Not Used 1-User Configured 2-Low Fuel LVL Switch 3-Low Lube Oil Press Switch 4-High Engine Temp Switch 5-Low Water LVL Switch 6-Emergency Stop 7-Remote Start / Stop 8-Simulate Start 9-Simulate Stop 10-Simulate Auto 11-Close Gen/Open Mains Switch 12-Close Mains/Open Gen Switch 13-Simulate Mains 14-V-Belt Broken Switch 15-Mains Contactor Latched 16-Genset Contactor Latched 17-Battery Charger Fail 18-Smoke Fire 19-Mode Select Switch 20-Ambient Temp. Switch 21-EGR Digital In 22-EB MCCB On Feedback 23-DG MCCB On Feedback 24-Supercapacitor Fail | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | Dig In H , |  |  | Emergency Stop,
|  |  | Polarity |  |  | 0 | 0 – Close to activate 1 – Open to activate | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | Dig In I , |  |  | Remote Start / Stop,
|  |  | Action |  |  | 0 | 0 – None 1 – Warning 2 – Electrical trip 3 – Shutdown 4 – Notification | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | Dig In J (LOP Resistive) , |  |  | Simulate Start,
|  |  | Activation |  |  | 2 | 0 – Never 1 – From Engine start 2 – From monitoring On 3 – Always | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | Dig In K (Anlg In Fuel LVL), |  |  | Simulate Stop,
|  |  | Activation Delay (Sec) | 1 | 180 | 1 |  | uint8 | sec | Pass | Sahil Sheikh | 2024-03-20 |  |  | Dig In L (Anlg In Eng Temp), |  |  | Simulate Auto,
Digital Input F
|  |  | Source |  |  | 0 | 0-Not Used 1-User Configured 2-Low Fuel LVL Switch 3-Low Lube Oil Press Switch 4-High Engine Temp Switch 5-Low Water LVL Switch 6-Emergency Stop 7-Remote Start / Stop 8-Simulate Start 9-Simulate Stop 10-Simulate Auto 11-Close Gen/Open Mains Switch 12-Close Mains/Open Gen Switch 13-Simulate Mains 14-V-Belt Broken Switch 15-Mains Contactor Latched 16-Genset Contactor Latched 17-Battery Charger Fail 18-Smoke Fire 19-Mode Select Switch 20-Ambient Temp. Switch 21-EGR Digital In 22-EB MCCB On Feedback 23-DG MCCB On Feedback 24-Supercapacitor Fail | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | Dig In M (Auxiliary Sensor 1), |  |  | Close Gen/Open Mains Switch,
|  |  | Polarity |  |  | 0 | 0 – Close to activate 1 – Open to activate | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | Dig In N (Auxiliary Sensor 2), |  |  | Close Mains/Open Gen Switch,
|  |  | Action |  |  | 0 | 0 – None 1 – Warning 2 – Electrical trip 3 – Shutdown 4 – Notification | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | Dig In O (Auxiliary Sensor 3), |  |  | Simulate Mains,
|  |  | Activation |  |  | 2 | 0 – Never 1 – From Engine start 2 – From monitoring On 3 – Always | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | Dig In P (Auxiliary Sensor 4), |  |  | V-Belt Broken Switch,
|  |  | Activation Delay (Sec) | 1 | 180 | 1 |  | uint8 | sec | Pass | Sahil Sheikh | 2024-03-20 |  |  | Emergency Stop, |  |  | Mains Contactor Latched,
Digital Input G
|  |  | Source |  |  | 0 | 0-Not Used 1-User Configured 2-Low Fuel LVL Switch 3-Low Lube Oil Press Switch 4-High Engine Temp Switch 5-Low Water LVL Switch 6-Emergency Stop 7-Remote Start / Stop 8-Simulate Start 9-Simulate Stop 10-Simulate Auto 11-Close Gen/Open Mains Switch 12-Close Mains/Open Gen Switch 13-Simulate Mains 14-V-Belt Broken Switch 15-Mains Contactor Latched 16-Genset Contactor Latched 17-Battery Charger Fail 18-Smoke Fire 19-Mode Select Switch 20-Ambient Temp. Switch 21-EGR Digital In 22-EB MCCB On Feedback 23-DG MCCB On Feedback 24-Supercapacitor Fail | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | Stop Solenoid, |  |  | Genset Contactor Latched,
|  |  | Polarity |  |  | 0 | 0 – Close to activate 1 – Open to activate | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | To Start, |  |  | Battery Charger ,
|  |  | Action |  |  | 0 | 0 – None 1 – Warning 2 – Electrical trip 3 – Shutdown 4 – Notification | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | To Stop, |  |  | Smoke Fire,
|  |  | Activation |  |  | 2 | 0 – Never 1 – From Engine start 2 – From monitoring On 3 – Always | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | Fuel Relay, |  |  | Mode Select Switch,
|  |  | Activation Delay (Sec) | 1 | 180 | 1 |  | uint8 | sec | Pass | Sahil Sheikh | 2024-03-20 |  |  | Gen Available, |  |  | Ambient Temp. Switch,
|  | Digital Input H | [15 empty] | EB MCCB On Feedback",
|  |  | Source |  |  | 0 | 0-Not Used 1-User Configured 2-Low Fuel LVL Switch 3-Low Lube Oil Press Switch 4-High Engine Temp Switch 5-Low Water LVL Switch 6-Emergency Stop 7-Remote Start / Stop 8-Simulate Start 9-Simulate Stop 10-Simulate Auto 11-Close Gen/Open Mains Switch 12-Close Mains/Open Gen Switch 13-Simulate Mains 14-V-Belt Broken Switch 15-Mains Contactor Latched 16-Genset Contactor Latched 17-Battery Charger Fail 18-Smoke Fire 19-Mode Select Switch 20-Ambient Temp. Switch 21-EGR Digital In 22-EB MCCB On Feedback 23-DG MCCB On Feedback 24-Supercapacitor Fail | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | R Phase OV Shutdown, |  |  | "DG MCCB On Feedback
|  |  | Polarity |  |  | 0 | 0 – Close to activate 1 – Open to activate | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | R Phase UV Shutdown,
|  |  | Action |  |  | 0 | 0 – None 1 – Warning 2 – Electrical trip 3 – Shutdown 4 – Notification | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | Y Phase OV Shutdown,
|  |  | Activation |  |  | 2 | 0 – Never 1 – From Engine start 2 – From monitoring On 3 – Always | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | Y Phase UV Shutdown,
|  |  | Activation Delay (Sec) | 1 | 180 | 1 |  | uint8 | sec | Pass | Sahil Sheikh | 2024-03-20 |  |  | B Phase OV Shutdown,
|  | Digital Input I | [12 empty] | B Phase UV Shutdown,
|  |  | Source |  |  | 0 | 0-Not Used 1-User Configured 2-Low Fuel LVL Switch 3-Low Lube Oil Press Switch 4-High Engine Temp Switch 5-Low Water LVL Switch 6-Emergency Stop 7-Remote Start / Stop 8-Simulate Start 9-Simulate Stop 10-Simulate Auto 11-Close Gen/Open Mains Switch 12-Close Mains/Open Gen Switch 13-Simulate Mains 14-V-Belt Broken Switch 15-Mains Contactor Latched 16-Genset Contactor Latched 17-Battery Charger Fail 18-Smoke Fire 19-Mode Select Switch 20-Ambient Temp. Switch 21-EGR Digital In 22-EB MCCB On Feedback 23-DG MCCB On Feedback 24-Supercapacitor Fail | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | Gen Over Current ,
|  |  | Polarity |  |  | 0 | 0 – Close to activate 1 – Open to activate | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | High Engine Temp,
|  |  | Action |  |  | 0 | 0 – None 1 – Warning 2 – Electrical trip 3 – Shutdown 4 – Notification | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | Low Fuel LVL,
|  |  | Activation |  |  | 2 | 0 – Never 1 – From Engine start 2 – From monitoring On 3 – Always | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | LFL Sensor Notification,
|  |  | Activation Delay (Sec) | 1 | 180 | 1 |  | uint8 | sec | Pass | Sahil Sheikh | 2024-03-20 |  |  | Low LOP,
| Analog Inputs | [13 empty] | Mains High Volt,
|  | LOP / DIG J | [12 empty] | Mains Low Volt,
|  |  | Sensor Selection |  |  | 0 | 0-Not Used 1-Digital Input J 2-Lube Oil Pressure | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | Pressure Open Circuit,
|  |  | Source |  |  | 0 | 0-Not Used 1-User Configured 2-Low Fuel LVL Switch 3-Low Lube Oil Press Switch 4-High Engine Temp Switch 5-Low Water LVL Switch 6-Emergency Stop 7-Remote Start / Stop 8-Simulate Start 9-Simulate Stop 10-Simulate Auto 11-Close Gen/Open Mains Switch 12-Close Mains/Open Gen Switch 13-Simulate Mains 14-V-Belt Broken Switch 15-Mains Contactor Latched 16-Genset Contactor Latched 17-Battery Charger 18-Smoke Fire 19-Mode Select Switch 20-Ambient Temp. Switch 21-EB MCCB On Feedback 22-DG MCCB On Feedback | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | Open Gen Contactor,
|  |  | Polarity |  |  | 0 | 0 – Close to activate 1 – Open to activate | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | Open Mains Contactor,
|  |  | Action |  |  | 0 | 0 – None 1 – Warning 2 – Electrical trip 3 – Shutdown 4 – Notification | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | Over Freq Shutdown,
|  |  | Activation |  |  | 2 | 0 – Never 1 – From Engine start 2 – From monitoring On 3 – Always | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20 |  |  | Over Speed Shutdown,
|  |  | Activation Delay(Sec) | 1 | 180 | 1 |  | uint8 | sec | Pass | Sahil Sheikh | 2024-03-20 |  |  | Gross Over Speed Shutdown,
|  |  | LOP Shutdown |  |  | 1 | 0-Disable 1- Enable | uint8 | NA | Pass | Sangeet Wankhede | 2024-06-18 |  |  | Start Relay,
|  |  | LOP Shutdown threshold (bar) | 0 | 9.8 | 2 |  | float | bar | Pass | Sangeet Wankhede | 2024-06-18 |  |  | Temp Sensor Open Circuit,
|  |  | LOP Warning |  |  | 1 | 0-Disable 1- Enable | uint8 | NA | Pass | Sangeet Wankhede | 2024-06-18 |  |  | Under Freq Shutdown,
|  |  | LOP Warning threshold (bar) | 0.2 | 10 | 3 |  | float | bar | Pass | Sangeet Wankhede | 2024-06-18 |  |  | Under Speed Shutdown,
|  |  | LOP Sensor Open Ckt Alarm |  |  | 0 | 0-None 1- Warning 2-Shutdown | uint8 | NA | Pass | Sangeet Wankhede | 2024-06-18 |  |  | Maintenance Due,
|  |  | R1 | 0 | 1000 | 10 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01 |  |  | Stop Mode,
|  |  | V1 | 0 | 10 | 0 |  | float | bar | Pass | Sahil Sheikh | 2024-04-01 |  |  | Auto Mode,
|  |  | R2 | 0 | 1000 | 30 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01 |  |  | Manual Mode,
|  |  | V2 | 0 | 10 | 1 |  | float | bar | Pass | Sahil Sheikh | 2024-04-01 |  |  | BTS Mode,
|  |  | R3 | 0 | 1000 | 40 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01 |  |  | Preheat Output,
|  |  | V3 | 0 | 10 | 2 |  | float | bar | Pass | Sahil Sheikh | 2024-04-01 |  |  | ECU Start,
|  |  | R4 | 0 | 1000 | 64 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01 |  |  | Malfunction Indicator Lamp
|  |  | V4 | 0 | 10 | 3 |  | float | bar | Pass | Sahil Sheikh | 2024-04-01
|  |  | R5 | 0 | 1000 | 80 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | V5 | 0 | 10 | 4 |  | float | bar | Pass | Sahil Sheikh | 2024-04-01
|  |  | R6 | 0 | 1000 | 96 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | V6 | 0 | 10 | 5 |  | float | bar | Pass | Sahil Sheikh | 2024-04-01
|  |  | R7 | 0 | 1000 | 96 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | V7 | 0 | 10 | 5 |  | float | bar | Pass | Sahil Sheikh | 2024-04-01
|  |  | R8 | 0 | 1000 | 96 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | V8 | 0 | 10 | 5 |  | float | bar | Pass | Sahil Sheikh | 2024-04-01
|  |  | R9 | 0 | 1000 | 96 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | V9 | 0 | 10 | 5 |  | float | bar | Pass | Sahil Sheikh | 2024-04-01
|  |  | R10 | 0 | 1000 | 96 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | V10 | 0 | 10 | 5 |  | float | bar | Pass | Sahil Sheikh | 2024-04-01
Fuel Level / DIG K
|  |  | Sensor selection |  |  | 0 | 0-Not Used 1-Digital Input K 2-Fuel Level Sensor | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Source |  |  | 0 | 0-Not Used 1-User Configured 2-Low Fuel LVL Switch 3-Low Lube Oil Press Switch 4-High Engine Temp Switch 5-Low Water LVL Switch 6-Emergency Stop 7-Remote Start / Stop 8-Simulate Start 9-Simulate Stop 10-Simulate Auto 11-Close Gen/Open Mains Switch 12-Close Mains/Open Gen Switch 13-Simulate Mains 14-V-Belt Broken Switch 15-Mains Contactor Latched 16-Genset Contactor Latched 17-Battery Charger 18-Smoke Fire 19-Mode Select Switch 20-Ambient Temp. Switch 21-EB MCCB On Feedback 22-DG MCCB On Feedback | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Polarity |  |  | 0 | 0 – Close to activate 1 – Open to activate | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Action |  |  | 0 | 0 – None 1 – Warning 2 – Electrical trip 3 – Shutdown 4 – Notification | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Activation |  |  | 2 | 0 – Never 1 – From Engine start 2 – From monitoring On 3 – Always | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Activation Delay (Sec) | 1 | 180 | 1 |  | uint8 | sec | Pass | Sahil Sheikh | 2024-03-20
|  | Fuel Level Monitoring | Low Fuel Level Shutdown |  |  | 1 | 0-Disable 1-Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | Low Fuel Level Shutdown threshold (%) | 0 | 78 | 10 |  | uint8 | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | Low Fuel Level Notification |  |  | 1 | 0-Disable 1-Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | Low Fuel Level Notification threshold (%) | 2 | 80 | 12 |  | uint8 | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | Fuel Tank Capacity (Litre) | 2 | 1000 | 100 |  | uint16 | Litres | Pass | Sahil Sheikh | 2024-04-01
|  |  | Fuel Theft Warning |  |  | 1 | 0-Disable 1-Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | Fuel Theft Threshold (%/Hr) | 1 | 100 | 50 |  | uint8 | %/Hr | Pass | Sahil Sheikh | 2024-04-01
|  |  | Fuel Consumption (Ltr/Hr) | 0 | 100 | 50 |  | float | Ltr/Hr | Pass | Sahil Sheikh | 2024-04-01
|  |  | Display Fuel In % |  |  | 0 | 0-Disable 1-Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | R1 | 0 | 1000 | 14 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | L1 | 0 | 100 | 0 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | R2 | 0 | 1000 | 18 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | L2 | 0 | 100 | 5 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | R3 | 0 | 1000 | 22 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | L3 | 0 | 100 | 10 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | R4 | 0 | 1000 | 29 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | L4 | 0 | 100 | 15 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | R5 | 0 | 1000 | 37 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | L5 | 0 | 100 | 20 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | R6 | 0 | 1000 | 55 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | L6 | 0 | 100 | 25 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | R7 | 0 | 1000 | 74 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | L7 | 0 | 100 | 30 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | R8 | 0 | 1000 | 92 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | L8 | 0 | 100 | 35 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | R9 | 0 | 1000 | 110 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | L9 | 0 | 100 | 40 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | R10 | 0 | 1000 | 124 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | L10 | 0 | 100 | 45 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | R11 | 0 | 1000 | 139 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | L11 | 0 | 100 | 50 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | R12 | 0 | 1000 | 149 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | L12 | 0 | 100 | 55 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | R13 | 0 | 1000 | 159 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | L13 | 0 | 100 | 60 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | R14 | 0 | 1000 | 165 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | L14 | 0 | 100 | 65 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | R15 | 0 | 1000 | 171 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | L15 | 0 | 100 | 70 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | R16 | 0 | 1000 | 172 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | L16 | 0 | 100 | 75 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | R17 | 0 | 1000 | 174 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | L17 | 0 | 100 | 80 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | R18 | 0 | 1000 | 177 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | L18 | 0 | 100 | 85 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | R19 | 0 | 1000 | 180 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | L19 | 0 | 100 | 90 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | R20 | 0 | 1000 | 184 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | L20 | 0 | 100 | 100 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
Engine Temp / DIG L
|  |  | Sensor selection |  |  | 0 | 0-Not Used 1-Digital Input L 2- Engine Temperature Sensor | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Source |  |  | 0 | 0-Not Used 1-User Configured 2-Low Fuel LVL Switch 3-Low Lube Oil Press Switch 4-High Engine Temp Switch 5-Low Water LVL Switch 6-Emergency Stop 7-Remote Start / Stop 8-Simulate Start 9-Simulate Stop 10-Simulate Auto 11-Close Gen/Open Mains Switch 12-Close Mains/Open Gen Switch 13-Simulate Mains 14-V-Belt Broken Switch 15-Mains Contactor Latched 16-Genset Contactor Latched 17-Battery Charger 18-Smoke Fire 19-Mode Select Switch 20-Ambient Temp. Switch 21-EB MCCB On Feedback 22-DG MCCB On Feedback | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Polarity |  |  | 0 | 0 – Close to activate 1 – Open to activate | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Action |  |  | 0 | 0 – None 1 – Warning 2 – Electrical trip 3 – Shutdown 4 – Notification | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Activation |  |  | 2 | 0 – Never 1 – From Engine start 2 – From monitoring On 3 – Always | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Activation Delay (Sec) | 1 | 180 | 1 |  | uint8 | Sec | Pass | Sahil Sheikh | 2024-03-20
|  | Temp Sensor | High Temp. Action |  |  | 0 | 0-None 1- warning 2-Shutdown | uint8 | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | High temp. threshold | 25 | 300 | 25 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | Engine Temp Open Ckt Alarm |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | R1 | 0 | 5000 | 35 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | T1 | -5 | 300 | 125 |  | float | °C | Pass | Sahil Sheikh | 2024-04-01
|  |  | R2 | 0 | 5000 | 50 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | T2 | -5 | 300 | 110 |  | float | °C | Pass | Sahil Sheikh | 2024-04-01
|  |  | R3 | 0 | 5000 | 70 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | T3 | -5 | 300 | 100 |  | float | °C | Pass | Sahil Sheikh | 2024-04-01
|  |  | R4 | 0 | 5000 | 93 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | T4 | -5 | 300 | 90 |  | float | °C | Pass | Sahil Sheikh | 2024-04-01
|  |  | R5 | 0 | 5000 | 120 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | T5 | -5 | 300 | 85 |  | float | °C | Pass | Sahil Sheikh | 2024-04-01
|  |  | R6 | 0 | 5000 | 220 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | T6 | -5 | 300 | 65 |  | float | °C | Pass | Sahil Sheikh | 2024-04-01
|  |  | R7 | 0 | 5000 | 458 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | T7 | -5 | 300 | 45 |  | float | °C | Pass | Sahil Sheikh | 2024-04-01
|  |  | R8 | 0 | 5000 | 700 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | T8 | -5 | 300 | 35 |  | float | °C | Pass | Sahil Sheikh | 2024-04-01
|  |  | R9 | 0 | 5000 | 850 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | T9 | -5 | 300 | 35 |  | float | °C | Pass | Sahil Sheikh | 2024-04-01
|  |  | R10 | 0 | 5000 | 1000 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | T10 | -5 | 300 | 35 |  | float | °C | Pass | Sahil Sheikh | 2024-04-01
Shelter Temp Sensor / Dig M
|  |  | Sensor Selection |  |  | 0 | 0-Not Used 1-Digital Input M 2-Shelter Temperature Sensor | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Source |  |  | 0 | 0-Not Used 1-User Configured 2-Low Fuel LVL Switch 3-Low Lube Oil Press Switch 4-High Engine Temp Switch 5-Low Water LVL Switch 6-Emergency Stop 7-Remote Start / Stop 8-Simulate Start 9-Simulate Stop 10-Simulate Auto 11-Close Gen/Open Mains Switch 12-Close Mains/Open Gen Switch 13-Simulate Mains 14-V-Belt Broken Switch 15-Mains Contactor Latched 16-Genset Contactor Latched 17-Battery Charger 18-Smoke Fire 19-Mode Select Switch 20-Ambient Temp. Switch 21-EB MCCB On Feedback 22-DG MCCB On Feedback | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Polarity |  |  | 0 | 0 – Close to activate 1 – Open to activate | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Action |  |  | 0 | 0 – None 1 – Warning 2 – Electrical trip 3 – Shutdown 4 – Notification | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Activation |  |  | 2 | 0 – Never 1 – From Engine start 2 – From monitoring On 3 – Always | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Activation Delay(Sec) | 1 | 180 | 1 |  | uint8 | Sec | Pass | Sahil Sheikh | 2024-03-20
|  | Shelter Sensor Monitoring | High Temp Threshold | 20 | 60 | 60 |  | float | °C | Pass | Sahil Sheikh | 2024-04-01
|  |  | Low Temp Threshold | 18 | 55 | 55 |  | float | °C | Pass | Sahil Sheikh | 2024-04-01
|  |  | Shelt Temp Monitoring Delay(Sec) | 5 | 300 | 10 |  | uint16 | Sec | Pass | Sahil Sheikh | 2024-04-01
|  |  | Shelt Temp Run Duration | 1 | 720 | 2 |  | uint16 | min | Pass | Sahil Sheikh | 2024-04-01
|  |  | Circuit fault notification |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | R1 | 0 | 1000 | 1000 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | Val1 | -5 | 300 | 15 |  | float | °C | Pass | Sahil Sheikh | 2024-04-01
|  |  | R2 | 0 | 1000 | 841 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | Val2 | -5 | 300 | 20 |  | float | °C | Pass | Sahil Sheikh | 2024-04-01
|  |  | R3 | 0 | 1000 | 680 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | Val3 | -5 | 300 | 25 |  | float | °C | Pass | Sahil Sheikh | 2024-04-01
|  |  | R4 | 0 | 1000 | 554 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | Val4 | -5 | 300 | 30 |  | float | °C | Pass | Sahil Sheikh | 2024-04-01
|  |  | R5 | 0 | 1000 | 374 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | Val5 | -5 | 300 | 40 |  | float | °C | Pass | Sahil Sheikh | 2024-04-01
|  |  | R6 | 0 | 1000 | 311 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | Val6 | -5 | 300 | 45 |  | float | °C | Pass | Sahil Sheikh | 2024-04-01
|  |  | R7 | 0 | 1000 | 259 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | Val7 | -5 | 300 | 50 |  | float | °C | Pass | Sahil Sheikh | 2024-04-01
|  |  | R8 | 0 | 1000 | 218 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | Val8 | -5 | 300 | 55 |  | float | °C | Pass | Sahil Sheikh | 2024-04-01
|  |  | R9 | 0 | 1000 | 183 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | Val9 | -5 | 300 | 60 |  | float | °C | Pass | Sahil Sheikh | 2024-04-01
|  |  | R10 | 0 | 1000 | 156 |  | float | ohm | Pass | Sahil Sheikh | 2024-04-01
|  |  | Val10 | -5 | 300 | 65 |  | float | °C | Pass | Sahil Sheikh | 2024-04-01
S2 SENSOR / Dig N
|  |  | Sensor Selection |  |  | 0 | 0-Not Used 1-Digital Input N 2-S2 Sensor | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Source |  |  | 0 | 0-Not Used 1-User Configured 2-Low Fuel LVL Switch 3-Low Lube Oil Press Switch 4-High Engine Temp Switch 5-Low Water LVL Switch 6-Emergency Stop 7-Remote Start / Stop 8-Simulate Start 9-Simulate Stop 10-Simulate Auto 11-Close Gen/Open Mains Switch 12-Close Mains/Open Gen Switch 13-Simulate Mains 14-V-Belt Broken Switch 15-Mains Contactor Latched 16-Genset Contactor Latched 17-Battery Charger 18-Smoke Fire 19-Mode Select Switch 20-Ambient Temp. Switch 21-EB MCCB On Feedback 22-DG MCCB On Feedback | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Polarity |  |  | 0 | 0 – Close to activate 1 – Open to activate | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Action |  |  | 0 | 0 – None 1 – Warning 2 – Electrical trip 3 – Shutdown 4 – Notification | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Activation |  |  | 2 | 0 – Never 1 – From Engine start 2 – From monitoring On 3 – Always | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Activation Delay(Sec) | 1 | 180 | 1 |  | uint8 | Sec | Pass | Sahil Sheikh | 2024-03-20
|  | S2 SENSOR MONITORING | Action |  |  | 0 | 0 – None 1 – Warning 2 – Electrical trip 3 – Shutdown | uint8 | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | Threshold | 0 | 1000 | 100 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | Threshold Type |  |  | 0 | 0- Less than threshold 1-Greater than threshold | uint8 | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | OPEN CKT WARNING |  |  |  | 0-Disable 1- Enable |  | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | Sensor / Alarm name |  |  | S2 sensor |  | uint8 | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | R1 | 0 | 1000 | 0 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | Val1 | 0 | 1000 | 0 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | R2 | 0 | 1000 | 0 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | Val2 | 0 | 1000 | 0 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | R3 | 0 | 1000 | 0 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | Val3 | 0 | 1000 | 0 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | R4 | 0 | 1000 | 0 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | Val4 | 0 | 1000 | 0 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | R5 | 0 | 1000 | 0 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | Val5 | 0 | 1000 | 0 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | R6 | 0 | 1000 | 0 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | Val6 | 0 | 1000 | 0 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | R7 | 0 | 1000 | 0 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | Val7 | 0 | 1000 | 0 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | R8 | 0 | 1000 | 0 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | Val8 | 0 | 1000 | 0 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | R9 | 0 | 1000 | 0 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | Val9 | 0 | 1000 | 0 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | R10 | 0 | 1000 | 0 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
|  |  | Val10 | 0 | 1000 | 0 |  | float | NA | Pass | Sahil Sheikh | 2024-04-01
S3 SENSOR / Dig O
|  |  | Sensor Selection |  |  | 0 | 0-Not Used 1-Digital Input O 2-LOP (4-20mA) 3-LOP (0-5V) | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Source |  |  | 0 | 0-Not Used 1-User Configured 2-Low Fuel LVL Switch 3-Low Lube Oil Press Switch 4-High Engine Temp Switch 5-Low Water LVL Switch 6-Emergency Stop 7-Remote Start / Stop 8-Simulate Start 9-Simulate Stop 10-Simulate Auto 11-Close Gen/Open Mains Switch 12-Close Mains/Open Gen Switch 13-Simulate Mains 14-V-Belt Broken Switch 15-Mains Contactor Latched 16-Genset Contactor Latched 17-Battery Charger 18-Smoke Fire 19-Mode Select Switch 20-Ambient Temp. Switch 21-EB MCCB On Feedback 22-DG MCCB On Feedback | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Polarity |  |  | 0 | 0 – Close to activate 1 – Open to activate | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Action |  |  | 0 | 0 – None 1 – Warning 2 – Electrical trip 3 – Shutdown 4 – Notification | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Activation |  |  | 2 | 0 – Never 1 – From Engine start 2 – From monitoring On 3 – Always | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Activation Delay(Sec) | 1 | 180 | 1 |  | uint8 | sec | Pass | Sahil Sheikh | 2024-03-20
|  | LOP (4-20mA) | LOP Shutdown (4-20mA) |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | Pass | Sangeet Wankhede | 2024-06-18
|  |  | LOP Shutdown threshold (bar) | 0 | 9.8 | 2 |  | float | bar | Pass | Sangeet Wankhede | 2024-06-18
|  |  | LOP Warning |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | Pass | Sangeet Wankhede | 2024-06-18
|  |  | LOP Warning threshold (bar) | 0.2 | 10 | 3 |  | float | bar | Pass | Sangeet Wankhede | 2024-06-18
|  |  | Circuit Fault Action |  |  | 0 | 0-Warning 1-Shutdown | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | I1 | 4 | 20 | 4 |  | float | mA | Pass | Sahil Sheikh | 2024-03-20
|  |  | V1 | 0 | 10 | 0 |  | float | bar | Pass | Sahil Sheikh | 2024-03-20
|  |  | I2 | 4 | 20 | 6 |  | float | mA | Pass | Sahil Sheikh | 2024-03-20
|  |  | V2 | 0 | 10 | 1 |  | float | bar | Pass | Sahil Sheikh | 2024-03-20
|  |  | I3 | 4 | 20 | 7 |  | float | mA | Pass | Sahil Sheikh | 2024-03-20
|  |  | V3 | 0 | 10 | 2 |  | float | bar | Pass | Sahil Sheikh | 2024-03-20
|  |  | I4 | 4 | 20 | 9 |  | float | mA | Pass | Sahil Sheikh | 2024-03-20
|  |  | V4 | 0 | 10 | 3 |  | float | bar | Pass | Sahil Sheikh | 2024-03-20
|  |  | I5 | 4 | 20 | 10 |  | float | mA | Pass | Sahil Sheikh | 2024-03-20
|  |  | V5 | 0 | 10 | 4 |  | float | bar | Pass | Sahil Sheikh | 2024-03-20
|  |  | I6 | 4 | 20 | 12 |  | float | mA | Pass | Sahil Sheikh | 2024-03-20
|  |  | V6 | 0 | 10 | 5 |  | float | bar | Pass | Sahil Sheikh | 2024-03-20
|  |  | I7 | 4 | 20 | 14 |  | float | mA | Pass | Sahil Sheikh | 2024-03-20
|  |  | V7 | 0 | 10 | 6 |  | float | bar | Pass | Sahil Sheikh | 2024-03-20
|  |  | I8 | 4 | 20 | 15 |  | float | mA | Pass | Sahil Sheikh | 2024-03-20
|  |  | V8 | 0 | 10 | 7 |  | float | bar | Pass | Sahil Sheikh | 2024-03-20
|  |  | I9 | 4 | 20 | 17 |  | float | mA | Pass | Sahil Sheikh | 2024-03-20
|  |  | V9 | 0 | 10 | 8 |  | float | bar | Pass | Sahil Sheikh | 2024-03-20
|  |  | I10 | 4 | 20 | 20 |  | float | mA | Pass | Sahil Sheikh | 2024-03-20
|  |  | V10 | 0 | 10 | 10 |  | float | bar | Pass | Sahil Sheikh | 2024-03-20
|  | LOP(0-5V) | LOP Shutdown (0-5V) |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | Pass | Sangeet Wankhede | 2024-06-18
|  |  | LOP Shutdown threshold (bar) | 0 | 9.8 | 9.8 |  | float | bar | Pass | Sangeet Wankhede | 2024-06-18
|  |  | LOP Warning |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | Pass | Sangeet Wankhede | 2024-06-18
|  |  | LOP Warning threshold (bar) | 0 | 10 | 10 |  | float | bar | Pass | Sangeet Wankhede | 2024-06-18
|  |  | Circuit Fault Action |  |  | 0 | 0-None 1-Warning 2-Shutdown | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | I1 | 0 | 5 | 0.5 |  | float | volts | Pass | Sahil Sheikh | 2024-03-20
|  |  | V1 | 0 | 10 | 0 |  | float | bar | Pass | Sahil Sheikh | 2024-03-20
|  |  | I2 | 0 | 5 | 0.9 |  | float | volts | Pass | Sahil Sheikh | 2024-03-20
|  |  | V2 | 0 | 10 | 1 |  | float | bar | Pass | Sahil Sheikh | 2024-03-20
|  |  | I3 | 0 | 5 | 1.3 |  | float | volts | Pass | Sahil Sheikh | 2024-03-20
|  |  | V3 | 0 | 10 | 2 |  | float | bar | Pass | Sahil Sheikh | 2024-03-20
|  |  | I4 | 0 | 5 | 1.7 |  | float | volts | Pass | Sahil Sheikh | 2024-03-20
|  |  | V4 | 0 | 10 | 3 |  | float | bar | Pass | Sahil Sheikh | 2024-03-20
|  |  | I5 | 0 | 5 | 2.1 |  | float | volts | Pass | Sahil Sheikh | 2024-03-20
|  |  | V5 | 0 | 10 | 4 |  | float | bar | Pass | Sahil Sheikh | 2024-03-20
|  |  | I6 | 0 | 5 | 2.5 |  | float | volts | Pass | Sahil Sheikh | 2024-03-20
|  |  | V6 | 0 | 10 | 5 |  | float | bar | Pass | Sahil Sheikh | 2024-03-20
|  |  | I7 | 0 | 5 | 2.9 |  | float | volts | Pass | Sahil Sheikh | 2024-03-20
|  |  | V7 | 0 | 10 | 6 |  | float | bar | Pass | Sahil Sheikh | 2024-03-20
|  |  | I8 | 0 | 5 | 3.3 |  | float | volts | Pass | Sahil Sheikh | 2024-03-20
|  |  | V8 | 0 | 10 | 7 |  | float | bar | Pass | Sahil Sheikh | 2024-03-20
|  |  | I9 | 0 | 5 | 3.7 |  | float | volts | Pass | Sahil Sheikh | 2024-03-20
|  |  | V9 | 0 | 10 | 8 |  | float | bar | Pass | Sahil Sheikh | 2024-03-20
|  |  | I10 | 0 | 5 | 4.5 |  | float | volts | Pass | Sahil Sheikh | 2024-03-20
|  |  | V10 | 0 | 10 | 10 |  | float | bar | Pass | Sahil Sheikh | 2024-03-20
S4 SENSOR / Dig P
|  |  | Sensor Selection |  |  | 0 | 0-Not Used 1-Digital Input P 2-Lube Oil Pressure | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Source |  |  | 0 | 0-Not Used 1-User Configured 2-Low Fuel LVL Switch 3-Low Lube Oil Press Switch 4-High Engine Temp Switch 5-Low Water LVL Switch 6-Emergency Stop 7-Remote Start / Stop 8-Simulate Start 9-Simulate Stop 10-Simulate Auto 11-Close Gen/Open Mains Switch 12-Close Mains/Open Gen Switch 13-Simulate Mains 14-V-Belt Broken Switch 15-Mains Contactor Latched 16-Genset Contactor Latched 17-Battery Charger 18-Smoke Fire 19-Mode Select Switch 20-Ambient Temp. Switch 21-EB MCCB On Feedback 22-DG MCCB On Feedback | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Polarity |  |  | 0 | 0 – Close to activate 1 – Open to activate | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Action |  |  | 0 | 0 – None 1 – Warning 2 – Electrical trip 3 – Shutdown 4 – Notification | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Activation |  |  | 2 | 0 – Never 1 – From Engine start 2 – From monitoring On 3 – Always | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Activation Delay(Sec) | 1 | 180 | 1 |  | uint8 | sec | Pass | Sahil Sheikh | 2024-03-20
|  | Fuel Level Monitoring | Fuel Level Monitoring |  |  | 1 | 0-Disable 1- Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Low Fuel Level Shutdown threshold (%) | 0 | 78 | 10 |  | uint8 | % | Pass | Sahil Sheikh | 2024-03-20
|  |  | Low Fuel Level Notification |  |  | 1 | 0-Disable 1- Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Low Fuel Level Notification threshold (%) | 2 | 80 | 12 |  | uint8 | % | Pass | Sahil Sheikh | 2024-03-20
|  |  | Fuel Theft Alarm |  |  | 1 | 0-Disable 1- Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Fuel Theft Threshold (%/Hr) | 1 | 100 | 50 |  | uint8 | %/Hr | Pass | Sahil Sheikh | 2024-03-20
|  |  | Fuel Consumption (Ltr/Hr) | 0 | 100 | 50 |  | float | Ltr/Hr | Pass | Sahil Sheikh | 2024-03-20
|  |  | Display Fuel In Liters |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Sensor Low Voltage (Volt) (2 decimal) | 0 | 5 | 0 |  | float | volt | Pass | Sahil Sheikh | 2024-03-20
|  |  | Sensor High Voltage (Volt) | 0 | 5 | 5 |  | float | volt | Pass | Sahil Sheikh | 2024-03-20
|  |  | Tank With Step |  |  | 1 | 0-Disable 1- Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Tank Width (mm) - For Both Steps | 0 | 3000 | 600 |  | uint16 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Tank Step 1 Length (mm) | 0 | 3000 | 1000 |  | uint16 | mm | Pass | Sahil Sheikh | 2024-03-20
|  |  | Tank Step 1 Heigth (mm) | 0 | 3000 | 200 |  | uint16 | mm | Pass | Sahil Sheikh | 2024-03-20
|  |  | Tank Step 2 Length (mm) | 0 | 3000 | 600 |  | uint16 | mm | Pass | Sahil Sheikh | 2024-04-01
|  |  | Tank Step 2 Heigth (mm) | 0 | 3000 | 150 |  | uint16 | mm | Pass | Sahil Sheikh | 2024-04-01
Dig IN Q
|  |  | Source |  |  | 0 | 0-Not Used 1-User Configured 2-Low Fuel LVL Switch 3-Low Lube Oil Press Switch 4-High Engine Temp Switch 5-Low Water LVL Switch 6-Emergency Stop 7-Remote Start / Stop 8-Simulate Start 9-Simulate Stop 10-Simulate Auto 11-Close Gen/Open Mains Switch 12-Close Mains/Open Gen Switch 13-Simulate Mains 14-V-Belt Broken Switch 15-Mains Contactor Latched 16-Genset Contactor Latched 17-Battery Charger 18-Smoke Fire 19-Mode Select Switch 20-Ambient Temp. Switch 21-EB MCCB On Feedback 22-DG MCCB On Feedback | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Polarity |  |  | 0 | 0 – Close to activate 1 – Open to activate | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Action |  |  | 0 | 0 – None 1 – Warning 2 – Electrical trip 3 – Shutdown 4 – Notification | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Activation |  |  | 2 | 0 – Never 1 – From Engine start 2 – From monitoring On 3 – Always | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Activation Delay(Sec) | 1 | 180 | 1 |  | uint8 | sec | Pass | Sahil Sheikh | 2024-03-20
Dig IN R
|  |  | Source |  |  | 0 | 0-Not Used 1-User Configured 2-Low Fuel LVL Switch 3-Low Lube Oil Press Switch 4-High Engine Temp Switch 5-Low Water LVL Switch 6-Emergency Stop 7-Remote Start / Stop 8-Simulate Start 9-Simulate Stop 10-Simulate Auto 11-Close Gen/Open Mains Switch 12-Close Mains/Open Gen Switch 13-Simulate Mains 14-V-Belt Broken Switch 15-Mains Contactor Latched 16-Genset Contactor Latched 17-Battery Charger 18-Smoke Fire 19-Mode Select Switch 20-Ambient Temp. Switch 21-EB MCCB On Feedback 22-DG MCCB On Feedback | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Polarity |  |  | 0 | 0 – Close to activate 1 – Open to activate | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Action |  |  | 0 | 0 – None 1 – Warning 2 – Electrical trip 3 – Shutdown 4 – Notification | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Activation |  |  | 2 | 0 – Never 1 – From Engine start 2 – From monitoring On 3 – Always | uint8 | NA | Pass | Sahil Sheikh | 2024-03-20
|  |  | Activation Delay(Sec) | 1 | 180 | 1 |  | uint8 | sec | Pass | Sahil Sheikh | 2024-03-20
Outputs
Digital Output A
|  |  | Source |  |  | 0 | 0-Disable 1-Sounder Alarm 2-Battery Over Volt 3-Battery Under Volt 4-Charge Alt Shutdown 5-Charge Alt Warning 6-Close Gen Contactor 7-Close Mains Contactor 8-Mains ure 9-Common Alarm 10-Common Electric Trip 11-Common Shutdown 12-Common Warning 13-Cooling Down 14-Dig In A 15-Dig In B 16-Dig In C 17-Dig In D 18-Dig In E 19-Dig In F 20-Dig In G 21-Dig In H 22-Dig In I 23-Dig In J (LOP Resistive) 24-Dig In K (Anlg In Fuel LVL) 25-Dig In L (Anlg In Eng Temp) 26-Dig In M (Auxiliary Sensor 1) 27-Dig In N (Auxiliary Sensor 2) 28-Dig In O (Auxiliary Sensor 3) 29-Dig In P (Auxiliary Sensor 4) 30-Emergency Stop 31-Stop Solenoid 32- To Start 33- To Stop 34-Fuel Relay 35-Gen Available 36-R Phase OV Shutdown 37-R Phase UV Shutdown 38-Y Phase OV Shutdown 39-Y Phase UV Shutdown 40-B Phase OV Shutdown 41-B Phase UV Shutdown 42-Gen Over Current 43-High Engine Temp 44-Low Fuel LVL 45-LFL Sensor Notification 46-Low LOP 47-Mains High Volt 48-Mains Low Volt 49-Pressure Open Circuit 50-Open Gen Contactor 51-Open Mains Contactor 52-Over Freq Shutdown 53-Over Speed Shutdown 54-Gross Over Speed Shutdown 55-Start Relay 56-Temp Sensor Open Circuit 57-Under Freq Shutdown 58-Under Speed Shutdown 59-Maintenance Due 60-Stop Mode 61-Auto Mode 62-Manual Mode 63-BTS Mode 64-Preheat Output 65-ECU Start 66-Malfunction Indicator Lamp 67-Inducement Buzzer 68-Dig In Q 69-Dig In R | uint8 | NA | Pass | Sahil Sheikh | 2024-03-22
|  |  | Polarity |  |  | 0 | 0-De-energise 1- energise | uint8 | NA | Pass | Sahil Sheikh | 2024-03-22
Digital Output B
|  |  | Source |  |  | 0 | 0-Disable 1-Sounder Alarm 2-Battery Over Volt 3-Battery Under Volt 4-Charge Alt Shutdown 5-Charge Alt Warning 6-Close Gen Contactor 7-Close Mains Contactor 8-Mains ure 9-Common Alarm 10-Common Electric Trip 11-Common Shutdown 12-Common Warning 13-Cooling Down 14-Dig In A 15-Dig In B 16-Dig In C 17-Dig In D 18-Dig In E 19-Dig In F 20-Dig In G 21-Dig In H 22-Dig In I 23-Dig In J (LOP Resistive) 24-Dig In K (Anlg In Fuel LVL) 25-Dig In L (Anlg In Eng Temp) 26-Dig In M (Auxiliary Sensor 1) 27-Dig In N (Auxiliary Sensor 2) 28-Dig In O (Auxiliary Sensor 3) 29-Dig In P (Auxiliary Sensor 4) 30-Emergency Stop 31-Stop Solenoid 32- To Start 33- To Stop 34-Fuel Relay 35-Gen Available 36-R Phase OV Shutdown 37-R Phase UV Shutdown 38-Y Phase OV Shutdown 39-Y Phase UV Shutdown 40-B Phase OV Shutdown 41-B Phase UV Shutdown 42-Gen Over Current 43-High Engine Temp 44-Low Fuel LVL 45-LFL Sensor Notification 46-Low LOP 47-Mains High Volt 48-Mains Low Volt 49-Pressure Open Circuit 50-Open Gen Contactor 51-Open Mains Contactor 52-Over Freq Shutdown 53-Over Speed Shutdown 54-Gross Over Speed Shutdown 55-Start Relay 56-Temp Sensor Open Circuit 57-Under Freq Shutdown 58-Under Speed Shutdown 59-Maintenance Due 60-Stop Mode 61-Auto Mode 62-Manual Mode 63-BTS Mode 64-Preheat Output 65-ECU Start 66-Malfunction Indicator Lamp 67-Inducement Buzzer 68-Dig In Q 69-Dig In R | uint8 | NA | Pass | Sahil Sheikh | 2024-03-22
|  |  | Polarity |  |  | 0 | 0-De-energise 1- energise | uint8 | NA | Pass | Sahil Sheikh | 2024-03-22
Digital Output C
|  |  | Source |  |  | 0 | 0-Disable 1-Sounder Alarm 2-Battery Over Volt 3-Battery Under Volt 4-Charge Alt Shutdown 5-Charge Alt Warning 6-Close Gen Contactor 7-Close Mains Contactor 8-Mains ure 9-Common Alarm 10-Common Electric Trip 11-Common Shutdown 12-Common Warning 13-Cooling Down 14-Dig In A 15-Dig In B 16-Dig In C 17-Dig In D 18-Dig In E 19-Dig In F 20-Dig In G 21-Dig In H 22-Dig In I 23-Dig In J (LOP Resistive) 24-Dig In K (Anlg In Fuel LVL) 25-Dig In L (Anlg In Eng Temp) 26-Dig In M (Auxiliary Sensor 1) 27-Dig In N (Auxiliary Sensor 2) 28-Dig In O (Auxiliary Sensor 3) 29-Dig In P (Auxiliary Sensor 4) 30-Emergency Stop 31-Stop Solenoid 32- To Start 33- To Stop 34-Fuel Relay 35-Gen Available 36-R Phase OV Shutdown 37-R Phase UV Shutdown 38-Y Phase OV Shutdown 39-Y Phase UV Shutdown 40-B Phase OV Shutdown 41-B Phase UV Shutdown 42-Gen Over Current 43-High Engine Temp 44-Low Fuel LVL 45-LFL Sensor Notification 46-Low LOP 47-Mains High Volt 48-Mains Low Volt 49-Pressure Open Circuit 50-Open Gen Contactor 51-Open Mains Contactor 52-Over Freq Shutdown 53-Over Speed Shutdown 54-Gross Over Speed Shutdown 55-Start Relay 56-Temp Sensor Open Circuit 57-Under Freq Shutdown 58-Under Speed Shutdown 59-Maintenance Due 60-Stop Mode 61-Auto Mode 62-Manual Mode 63-BTS Mode 64-Preheat Output 65-ECU Start 66-Malfunction Indicator Lamp 67-Inducement Buzzer 68-Dig In Q 69-Dig In R | uint8 | NA | Pass | Sahil Sheikh | 2024-03-22
|  |  | Polarity |  |  | 0 | 0-De-energise 1- energise | uint8 | NA | Pass | Sahil Sheikh | 2024-03-22
Digital Output D
|  |  | Source |  |  | 0 | 0-Disable 1-Sounder Alarm 2-Battery Over Volt 3-Battery Under Volt 4-Charge Alt Shutdown 5-Charge Alt Warning 6-Close Gen Contactor 7-Close Mains Contactor 8-Mains ure 9-Common Alarm 10-Common Electric Trip 11-Common Shutdown 12-Common Warning 13-Cooling Down 14-Dig In A 15-Dig In B 16-Dig In C 17-Dig In D 18-Dig In E 19-Dig In F 20-Dig In G 21-Dig In H 22-Dig In I 23-Dig In J (LOP Resistive) 24-Dig In K (Anlg In Fuel LVL) 25-Dig In L (Anlg In Eng Temp) 26-Dig In M (Auxiliary Sensor 1) 27-Dig In N (Auxiliary Sensor 2) 28-Dig In O (Auxiliary Sensor 3) 29-Dig In P (Auxiliary Sensor 4) 30-Emergency Stop 31-Stop Solenoid 32- To Start 33- To Stop 34-Fuel Relay 35-Gen Available 36-R Phase OV Shutdown 37-R Phase UV Shutdown 38-Y Phase OV Shutdown 39-Y Phase UV Shutdown 40-B Phase OV Shutdown 41-B Phase UV Shutdown 42-Gen Over Current 43-High Engine Temp 44-Low Fuel LVL 45-LFL Sensor Notification 46-Low LOP 47-Mains High Volt 48-Mains Low Volt 49-Pressure Open Circuit 50-Open Gen Contactor 51-Open Mains Contactor 52-Over Freq Shutdown 53-Over Speed Shutdown 54-Gross Over Speed Shutdown 55-Start Relay 56-Temp Sensor Open Circuit 57-Under Freq Shutdown 58-Under Speed Shutdown 59-Maintenance Due 60-Stop Mode 61-Auto Mode 62-Manual Mode 63-BTS Mode 64-Preheat Output 65-ECU Start 66-Malfunction Indicator Lamp 67-Inducement Buzzer 68-Dig In Q 69-Dig In R | uint8 | NA | Pass | Sahil Sheikh | 2024-03-22
|  |  | Polarity |  |  | 0 | 0-De-energise 1- energise | uint8 | NA | Pass | Sahil Sheikh | 2024-03-22
Digital Output E
|  |  | Source |  |  | 0 | 0-Disable 1-Sounder Alarm 2-Battery Over Volt 3-Battery Under Volt 4-Charge Alt Shutdown 5-Charge Alt Warning 6-Close Gen Contactor 7-Close Mains Contactor 8-Mains ure 9-Common Alarm 10-Common Electric Trip 11-Common Shutdown 12-Common Warning 13-Cooling Down 14-Dig In A 15-Dig In B 16-Dig In C 17-Dig In D 18-Dig In E 19-Dig In F 20-Dig In G 21-Dig In H 22-Dig In I 23-Dig In J (LOP Resistive) 24-Dig In K (Anlg In Fuel LVL) 25-Dig In L (Anlg In Eng Temp) 26-Dig In M (Auxiliary Sensor 1) 27-Dig In N (Auxiliary Sensor 2) 28-Dig In O (Auxiliary Sensor 3) 29-Dig In P (Auxiliary Sensor 4) 30-Emergency Stop 31-Stop Solenoid 32- To Start 33- To Stop 34-Fuel Relay 35-Gen Available 36-R Phase OV Shutdown 37-R Phase UV Shutdown 38-Y Phase OV Shutdown 39-Y Phase UV Shutdown 40-B Phase OV Shutdown 41-B Phase UV Shutdown 42-Gen Over Current 43-High Engine Temp 44-Low Fuel LVL 45-LFL Sensor Notification 46-Low LOP 47-Mains High Volt 48-Mains Low Volt 49-Pressure Open Circuit 50-Open Gen Contactor 51-Open Mains Contactor 52-Over Freq Shutdown 53-Over Speed Shutdown 54-Gross Over Speed Shutdown 55-Start Relay 56-Temp Sensor Open Circuit 57-Under Freq Shutdown 58-Under Speed Shutdown 59-Maintenance Due 60-Stop Mode 61-Auto Mode 62-Manual Mode 63-BTS Mode 64-Preheat Output 65-ECU Start 66-Malfunction Indicator Lamp 67-Inducement Buzzer 68-Dig In Q 69-Dig In R | uint8 | NA | Pass | Sahil Sheikh | 2024-03-22
|  |  | Polarity |  |  | 0 | 0-De-energise 1- energise | uint8 | NA | Pass | Sahil Sheikh | 2024-03-22
Digital Output F
|  |  | Source |  |  | 0 | 0-Disable 1-Sounder Alarm 2-Battery Over Volt 3-Battery Under Volt 4-Charge Alt Shutdown 5-Charge Alt Warning 6-Close Gen Contactor 7-Close Mains Contactor 8-Mains ure 9-Common Alarm 10-Common Electric Trip 11-Common Shutdown 12-Common Warning 13-Cooling Down 14-Dig In A 15-Dig In B 16-Dig In C 17-Dig In D 18-Dig In E 19-Dig In F 20-Dig In G 21-Dig In H 22-Dig In I 23-Dig In J (LOP Resistive) 24-Dig In K (Anlg In Fuel LVL) 25-Dig In L (Anlg In Eng Temp) 26-Dig In M (Auxiliary Sensor 1) 27-Dig In N (Auxiliary Sensor 2) 28-Dig In O (Auxiliary Sensor 3) 29-Dig In P (Auxiliary Sensor 4) 30-Emergency Stop 31-Stop Solenoid 32- To Start 33- To Stop 34-Fuel Relay 35-Gen Available 36-R Phase OV Shutdown 37-R Phase UV Shutdown 38-Y Phase OV Shutdown 39-Y Phase UV Shutdown 40-B Phase OV Shutdown 41-B Phase UV Shutdown 42-Gen Over Current 43-High Engine Temp 44-Low Fuel LVL 45-LFL Sensor Notification 46-Low LOP 47-Mains High Volt 48-Mains Low Volt 49-Pressure Open Circuit 50-Open Gen Contactor 51-Open Mains Contactor 52-Over Freq Shutdown 53-Over Speed Shutdown 54-Gross Over Speed Shutdown 55-Start Relay 56-Temp Sensor Open Circuit 57-Under Freq Shutdown 58-Under Speed Shutdown 59-Maintenance Due 60-Stop Mode 61-Auto Mode 62-Manual Mode 63-BTS Mode 64-Preheat Output 65-ECU Start 66-Malfunction Indicator Lamp 67-Inducement Buzzer 68-Dig In Q 69-Dig In R | uint8 | NA | Pass | Sahil Sheikh | 2024-03-22
|  |  | Polarity |  |  | 0 | 0-De-energise 1- energise | uint8 | NA | Pass | Sahil Sheikh | 2024-03-22
Digital Output G
|  |  | Source |  |  | 0 | 0-Disable 1-Sounder Alarm 2-Battery Over Volt 3-Battery Under Volt 4-Charge Alt Shutdown 5-Charge Alt Warning 6-Close Gen Contactor 7-Close Mains Contactor 8-Mains ure 9-Common Alarm 10-Common Electric Trip 11-Common Shutdown 12-Common Warning 13-Cooling Down 14-Dig In A 15-Dig In B 16-Dig In C 17-Dig In D 18-Dig In E 19-Dig In F 20-Dig In G 21-Dig In H 22-Dig In I 23-Dig In J (LOP Resistive) 24-Dig In K (Anlg In Fuel LVL) 25-Dig In L (Anlg In Eng Temp) 26-Dig In M (Auxiliary Sensor 1) 27-Dig In N (Auxiliary Sensor 2) 28-Dig In O (Auxiliary Sensor 3) 29-Dig In P (Auxiliary Sensor 4) 30-Emergency Stop 31-Stop Solenoid 32- To Start 33- To Stop 34-Fuel Relay 35-Gen Available 36-R Phase OV Shutdown 37-R Phase UV Shutdown 38-Y Phase OV Shutdown 39-Y Phase UV Shutdown 40-B Phase OV Shutdown 41-B Phase UV Shutdown 42-Gen Over Current 43-High Engine Temp 44-Low Fuel LVL 45-LFL Sensor Notification 46-Low LOP 47-Mains High Volt 48-Mains Low Volt 49-Pressure Open Circuit 50-Open Gen Contactor 51-Open Mains Contactor 52-Over Freq Shutdown 53-Over Speed Shutdown 54-Gross Over Speed Shutdown 55-Start Relay 56-Temp Sensor Open Circuit 57-Under Freq Shutdown 58-Under Speed Shutdown 59-Maintenance Due 60-Stop Mode 61-Auto Mode 62-Manual Mode 63-BTS Mode 64-Preheat Output 65-ECU Start 66-Malfunction Indicator Lamp 67-Inducement Buzzer 68-Dig In Q 69-Dig In R | uint8 | NA | Pass | Sahil Sheikh | 2024-03-22
|  |  | Polarity |  |  | 0 | 0-De-energise 1- energise | uint8 | NA | Pass | Sahil Sheikh | 2024-03-22
Digital Output H
|  |  | Source |  |  | 0 | 0-Disable 1-Sounder Alarm 2-Battery Over Volt 3-Battery Under Volt 4-Charge Alt Shutdown 5-Charge Alt Warning 6-Close Gen Contactor 7-Close Mains Contactor 8-Mains ure 9-Common Alarm 10-Common Electric Trip 11-Common Shutdown 12-Common Warning 13-Cooling Down 14-Dig In A 15-Dig In B 16-Dig In C 17-Dig In D 18-Dig In E 19-Dig In F 20-Dig In G 21-Dig In H 22-Dig In I 23-Dig In J (LOP Resistive) 24-Dig In K (Anlg In Fuel LVL) 25-Dig In L (Anlg In Eng Temp) 26-Dig In M (Auxiliary Sensor 1) 27-Dig In N (Auxiliary Sensor 2) 28-Dig In O (Auxiliary Sensor 3) 29-Dig In P (Auxiliary Sensor 4) 30-Emergency Stop 31-Stop Solenoid 32- To Start 33- To Stop 34-Fuel Relay 35-Gen Available 36-R Phase OV Shutdown 37-R Phase UV Shutdown 38-Y Phase OV Shutdown 39-Y Phase UV Shutdown 40-B Phase OV Shutdown 41-B Phase UV Shutdown 42-Gen Over Current 43-High Engine Temp 44-Low Fuel LVL 45-LFL Sensor Notification 46-Low LOP 47-Mains High Volt 48-Mains Low Volt 49-Pressure Open Circuit 50-Open Gen Contactor 51-Open Mains Contactor 52-Over Freq Shutdown 53-Over Speed Shutdown 54-Gross Over Speed Shutdown 55-Start Relay 56-Temp Sensor Open Circuit 57-Under Freq Shutdown 58-Under Speed Shutdown 59-Maintenance Due 60-Stop Mode 61-Auto Mode 62-Manual Mode 63-BTS Mode 64-Preheat Output 65-ECU Start 66-Malfunction Indicator Lamp 67-Inducement Buzzer 68-Dig In Q 69-Dig In R | uint8 | NA | Pass | Sahil Sheikh | 2024-03-22
|  |  | Polarity |  |  | 0 | 0-De-energise 1- energise | uint8 | NA | Pass | Sahil Sheikh | 2024-03-22
Digital Output I
|  |  | Source |  |  | 0 | 0-Disable 1-Sounder Alarm 2-Battery Over Volt 3-Battery Under Volt 4-Charge Alt Shutdown 5-Charge Alt Warning 6-Close Gen Contactor 7-Close Mains Contactor 8-Mains ure 9-Common Alarm 10-Common Electric Trip 11-Common Shutdown 12-Common Warning 13-Cooling Down 14-Dig In A 15-Dig In B 16-Dig In C 17-Dig In D 18-Dig In E 19-Dig In F 20-Dig In G 21-Dig In H 22-Dig In I 23-Dig In J (LOP Resistive) 24-Dig In K (Anlg In Fuel LVL) 25-Dig In L (Anlg In Eng Temp) 26-Dig In M (Auxiliary Sensor 1) 27-Dig In N (Auxiliary Sensor 2) 28-Dig In O (Auxiliary Sensor 3) 29-Dig In P (Auxiliary Sensor 4) 30-Emergency Stop 31-Stop Solenoid 32- To Start 33- To Stop 34-Fuel Relay 35-Gen Available 36-R Phase OV Shutdown 37-R Phase UV Shutdown 38-Y Phase OV Shutdown 39-Y Phase UV Shutdown 40-B Phase OV Shutdown 41-B Phase UV Shutdown 42-Gen Over Current 43-High Engine Temp 44-Low Fuel LVL 45-LFL Sensor Notification 46-Low LOP 47-Mains High Volt 48-Mains Low Volt 49-Pressure Open Circuit 50-Open Gen Contactor 51-Open Mains Contactor 52-Over Freq Shutdown 53-Over Speed Shutdown 54-Gross Over Speed Shutdown 55-Start Relay 56-Temp Sensor Open Circuit 57-Under Freq Shutdown 58-Under Speed Shutdown 59-Maintenance Due 60-Stop Mode 61-Auto Mode 62-Manual Mode 63-BTS Mode 64-Preheat Output 65-ECU Start 66-Malfunction Indicator Lamp 67-Inducement Buzzer 68-Dig In Q 69-Dig In R | uint8 | NA | Pass | Sahil Sheikh | 2024-03-22
|  |  | Polarity |  |  | 0 | 0-De-energise 1- energise | uint8 | NA | Pass | Sahil Sheikh | 2024-03-22
|  |  | Crank Hold Time (sec) | 1 | 10 | 4 |  | uint16 | sec | Pass | Sahil Sheikh | 2024-03-22
|  |  | Crank Rest Time (sec) | 2 | 60 | 10 |  | uint16 | sec | Pass | Sahil Sheikh | 2024-03-22
|  |  | Manual Start Delay (sec) | 1 | 10 | 3 |  | uint16 | sec | Pass | Sahil Sheikh | 2024-03-22
|  |  | Auto Start Delay (sec) | 1 | 10 | 5 |  | uint16 | sec | Pass | Sahil Sheikh | 2024-03-22
General
|  |  | Safety Monotoring Delay (sec) | 10 | 60 | 10 |  | uint16 | sec | Pass | Sahil Sheikh | 2024-03-22
|  |  | Mains Detect Delay (sec) | 1 | 20 | 5 |  | uint16 | sec | Pass | Sahil Sheikh | 2024-03-22
|  |  | Alternator Detect Delay (sec) | 1 | 30 | 5 |  | uint16 | sec | Pass | Sahil Sheikh | 2024-03-22
|  |  | Warm-up Delay (sec) | 10 | 60 | 30 |  | uint16 | sec | Pass | Sahil Sheikh | 2024-03-22
|  |  | Return To Mains Delay (sec) | 0 | 600 | 60 |  | uint16 | sec | Pass | Sahil Sheikh | 2024-03-22
|  |  | Engine Cooling Time (sec) | 59 | 300 | 60 |  | uint16 | sec | Pass | Sahil Sheikh | 2024-03-22
|  |  | Stop Action Time (sec) | 10 | 120 | 30 |  | uint16 | sec | Pass | Sahil Sheikh | 2024-03-22
|  |  | Additional Stopping Time (sec) | 0 | 120 | 10 |  | uint16 | sec | Pass | Sahil Sheikh | 2024-03-22
|  |  | Load Transfer Delay (sec) | 1 | 60 | 5 |  | uint16 | sec | Pass | Sahil Sheikh | 2024-03-22
|  |  | Power Save Mode Delay (sec) | 0 | 120 | 60 |  | uint16 | sec | Pass | Sahil Sheikh | 2024-03-22
|  |  | Screen Changeover Time (sec) | 0 | 60 | 30 |  | uint16 | sec | Pass | Sahil Sheikh | 2024-03-22
|  |  | Sounder Alarm Time (sec) | 1 | 300 | 60 |  | uint16 | sec | Pass | Sahil Sheikh | 2024-03-22
|  |  | Test Mode Timer (min) | 1 | 720 | 1 |  | uint16 | min | Pass | Sahil Sheikh | 2024-03-22
Generator
Alternator Config
|  |  | Alternator Present |  |  | 1 | 0- NO 1-Yes | uint8 | NA | Pass | Sahil Sheikh | 2024-03-22
|  |  | Number of Poles (options 4) |  |  | 1 | 0-2 1-4 2-6 3-8 | uint8 | NA | Pass | Sahil Sheikh | 2024-03-22
|  |  | AC System (opt 2) |  |  | 0 | 0-1 phase 1- 3 phase | uint8 | NA | Pass | Sahil Sheikh | 2024-03-22
|  |  | Min Healthy Voltage (volt) | 180 | 270 | 185 |  | uint16 | volt Ph-N | Pass | Sahil Sheikh | 2024-03-22
|  |  | Min Healthy Frequency (Hz) | 44 | 56 | 47 |  | uint8 | Hz | Pass | Sahil Sheikh | 2024-03-22
|  |  | Phase Reversal Detection |  |  | 0 | 0-Disable 1-Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-22
|  |  | Phase Reversal Action (opt 4) |  |  | 0 | 0 – None 1 – Warning 2– Electrical trip 3 – Shutdown | uint8 | NA | Pass | Sahil Sheikh | 2024-03-22
|  |  | Auto-load Transfer |  |  | 0 | 0-Disable 1-Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-22
|  |  | Alternator Wave Detection |  |  | 0 | 0-Disable 1-Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-22
Voltage Monitoring
|  |  | UV Shutdown Enable |  |  | 1 | 0-Disable 1-Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-22
|  |  | UV Shutdown Threshold (volt) | 180 | 225 | 184 |  | uint16 | volt Ph-N | Pass | Sahil Sheikh | 2024-03-22
|  |  | UV Warning Enable |  |  | 1 | 0-Disable 1-Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-22
|  |  | UV Warning Threshold (volt) | 185 | 230 | 189 |  | uint16 | volt Ph-N | Pass | Sahil Sheikh | 2024-03-22
|  |  | OV Shutdown Enable |  |  | 1 | 0-Disable 1-Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-22
|  |  | OV Shutdown Threshold (volt) | 235 | 270 | 264 |  | uint16 | volt Ph-N | Pass | Sahil Sheikh | 2024-03-22
|  |  | OV Warning Enable |  |  | 1 | 0-Disable 1-Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-22
|  |  | OV Warning Threshold(volt) | 230 | 265 | 260 |  | uint16 | volt Ph-N | Pass | Sahil Sheikh | 2024-03-22
Frequency Monitoring
|  |  | UF Shutdown Enable |  |  | 1 | 0-Disable 1-Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-22
|  |  | UF Shutdown Threshold (Hz) | 44 | 48 | 47 |  | float | Hz | Pass | Sahil Sheikh | 2024-03-22
|  |  | UF Warning Enable |  |  | 1 | 0-Disable 1-Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-22
|  |  | UF Warning Threshold (Hz) | 45 | 49 | 48 |  | float | Hz | Pass | Sahil Sheikh | 2024-03-22
|  |  | OF Shutdown Enable |  |  | 1 | 0-Disable 1-Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-22
|  |  | OF Shutdown Threshold (Hz) | 52 | 56 | 53 |  | float | Hz | Pass | Sahil Sheikh | 2024-03-22
|  |  | OF Warning Enable |  |  | 1 | 0-Disable 1-Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-22
|  |  | OF Warning Threshold (Hz) | 51 | 55 | 52 |  | float | Hz | Pass | Sahil Sheikh | 2024-03-22
Current monitoring
|  |  | CT Ratio | 0 | 8000 | 100 |  | uint16 | NA | Pass | Sahil Sheikh | 2024-03-22
|  |  | Over-current Action (opt 4) |  |  | 3 | 0 – None 1 – Warning 2– Electrical trip 3 – Shutdown | uint8 | NA | Pass | Sahil Sheikh | 2024-03-22
|  |  | Over-current Threshold (Amp) | 5 | 10000 | 44 |  | uint16 | Amp | Pass | Sahil Sheikh | 2024-03-22
|  |  | Over-current Delay (sec) | 1 | 600 | 3 |  | uint16 | sec | Pass | Sahil Sheikh | 2024-03-22
|  |  | CT Correction Factor | 0.9 | 1.1 | 1 |  | float | NA | Pass | Sahil Sheikh | 2024-03-22
|  |  | CT Location |  |  | 1 | 0-On alt output cable 1- On load cable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-22
Fan Current Monitoring
|  |  | Monitoring Enable |  |  | 1 | 0-Disable 1-Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | Fan CT Ratio | 0 | 8000 | 0 |  | uint16 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | Fan Current High Threshold | 0.1 | 10 | 0.2 |  | float | Amp | Pass | Sahil Sheikh | 2024-03-26
|  |  | Fan Current High Action (5 options) |  |  | 0 | 0 – None 1 – Warning 2 – Electrical trip 3 – Shutdown 4 – Notification | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | Fan Current Low Threshold | 0 | 9.9 | 0 |  | float | Amp | Pass | Sahil Sheikh | 2024-03-26
|  |  | Fan Current Low Action (opt 5) |  |  | 0 | 0 – None 1 – Warning 2 – Electrical trip 3 – Shutdown 4 – Notification | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | Fan Current Delay (sec) | 1 | 180 | 1 |  | uint16 | sec | Pass | Sahil Sheikh | 2024-03-26
Load Monitoring
|  |  | Generator Rating (kW) | 0 | 800 | 8 |  | uint16 | kw | Pass | Sahil Sheikh | 2024-03-26
|  |  | Full Load Current (Amp/Phase) | 1 | 800 | 1 |  | uint16 | Amp/Phase | Pass | Sahil Sheikh | 2024-03-26
|  |  | Over-load Action (opt 4) |  |  | 3 | 0 – None 1 – Warning 2– Electrical trip 3 – Shutdown | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | Load Monitoring Threshold (%) | 100 | 150 | 111 |  | uint16 | % | Pass | Sahil Sheikh | 2024-03-26
|  |  | Over-load Delay (sec) | 1 | 60 | 3 |  | uint16 | sec | Pass | Sahil Sheikh | 2024-03-26
|  |  | Unbalanced Load Action |  |  | 0 | 0 – None 1 – Warning 2– Electrical trip 3 – Shutdown | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | Unbalanced Load Threshold (%) | 5 | 100 | 25 |  | uint16 | % | Pass | Sahil Sheikh | 2024-03-26
|  |  | Unbalanced Load Delay (sec) | 1 | 60 | 10 |  | uint16 | sec | Pass | Sahil Sheikh | 2024-03-26
|  |  | Unbalanced Load Activation Threshold (%) | 0 | 100 | 60 |  | uint16 | % | Pass | Sahil Sheikh | 2024-03-26
Mains
Mains Config
|  |  | Mains Monitoring |  |  | 1 | 0-Disable 1-Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | Mains AC system (opt 2) |  |  | 1 | 0-1 phase 1- 3 phase | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | Phase Reversal Detection |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | Phase Reversal Action (opt 2) |  |  | 0 | 0-None 1-Notification | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | Three Phase calc for one phase |  |  | 1 | 0-Disable 1- Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
Under-voltage Monitoring
|  |  | Monitoring Enable |  |  | 1 | 0-Disable 1- Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | Under-voltage Trip (Volt) | 99 | 240 | 122 |  | uint16 | volt Ph-N | Pass | Sahil Sheikh | 2024-03-26
|  |  | Under-voltage Return (Volt) | 122 | 242 | 131 |  | uint16 | volt Ph-N | Pass | Sahil Sheikh | 2024-03-26
Over-voltage Monitoring
|  |  | Monitoring Enable |  |  | 1 | 0-Disable 1- Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | Over-voltage Trip (Volt) | 202 | 288 | 287 |  | uint16 | volt Ph-N | Pass | Sahil Sheikh | 2024-03-26
|  |  | Over-voltage Return (Volt) | 200 | 286 | 277 |  | uint16 | volt Ph-N | Pass | Sahil Sheikh | 2024-03-26
Under-frequency Monitoring
|  |  | Monitoring Enable |  |  | 1 | 0-Disable 1- Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | Under-frequency Trip (Hz) | 40 | 48 | 45 |  | float | Hz | Pass | Sahil Sheikh | 2024-03-26
|  |  | Under-frequency Return (Hz) | 41 | 49 | 46 |  | float | Hz | Pass | Sahil Sheikh | 2024-03-26
Over-frequency Monitoring
|  |  | Monitoring Enable |  |  | 1 | 0-Disable 1- Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | Over-frequency Trip (Hz) | 52 | 60 | 54 |  | float | Hz | Pass | Sahil Sheikh | 2024-03-26
|  |  | Over-frequency Return (Hz) | 51 | 59 | 53 |  | float | Hz | Pass | Sahil Sheikh | 2024-03-26
Engine
Crank Disconnect
|  |  | Start Attempts | 1 | 10 | 3 |  | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | Disconnect On LOP Sensor |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | Disconnect Pressure Threshold (bar) | 0.5 | 10 | 4 |  | float | bar | Pass | Sahil Sheikh | 2024-03-26
|  |  | Mon Pres Switch Before Start |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | Mon Pres Sensor Before Start |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | Disconnect On LLOP Switch |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | LLOP Switch Transient Time (sec) | 0 | 3 | 0.1 |  | float | sec | Pass | Sahil Sheikh | 2024-03-26
|  |  | Alternator Frequency (Hz) | 10 | 25 | 20 |  | uint16 | Hz | Pass | Sahil Sheikh | 2024-03-26
|  |  | Engine Speed (Speed) | 150 | 800 | 600 |  | uint16 | rpm | Pass | Sahil Sheikh | 2024-03-26
|  |  | Disconnect On Charging Alt Voltage |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | Charging Alt Voltage Threshold | 5 | 30 | 8 |  | float | volt | Pass | Sahil Sheikh | 2024-03-26
Speed Monitoring
|  |  | Engine Speed Sense Source (opt 1) |  |  | 0 | 0-Alternator Frequency | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | Under-speed Shutdown |  |  | 1 | 0-Disable 1- Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | Under-speed Threshold (RPM) | 1300 | 1500 | 1380 |  | uint16 | rpm | Pass | Sahil Sheikh | 2024-03-26
|  |  | Under-speed Delay (sec) | 1 | 60 | 10 |  | uint16 | sec | Pass | Sahil Sheikh | 2024-03-26
|  |  | Over-speed Threshold (RPM) | 1500 | 1680 | 1650 |  | uint16 | rpm | Pass | Sahil Sheikh | 2024-03-26
|  |  | Over-speed Delay (sec) | 1 | 20 | 10 |  | uint16 | sec | Pass | Sahil Sheikh | 2024-03-26
|  |  | Gross Over-speed Threshold (%) | 100 | 200 | 120 |  | uint16 | % | Pass | Sahil Sheikh | 2024-03-26
Battery Monitoring
|  |  | Low Battery voltage action |  |  | 4 | 0 – None 1 – Warning 2 – Electrical trip 3 – Shutdown 4 – Notification | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | Low Battery Voltage Threshold (volt) | 8 | 12 | 10 |  | float | volt | Pass | Sahil Sheikh | 2024-03-26
|  |  | Low Battery Voltage Delay (sec) | 5 | 1800 | 60 |  | uint16 | sec | Pass | Sahil Sheikh | 2024-03-26
|  |  | High Battery Voltage Action |  |  | 1 | 0 – None 1 – Warning 2 – Electrical trip 3 – Shutdown 4 – Notification | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | High Battery Voltage Threshold (volt) | 12 | 17 | 14 |  | float | volt | Pass | Sahil Sheikh | 2024-03-26
|  |  | High Battery Voltage Delay (sec) | 5 | 1800 | 30 |  | uint16 | sec | Pass | Sahil Sheikh | 2024-03-26
Charging Alt Monitoring
|  |  | Charging Alt Action (opt 5) |  |  | 4 | 0 – None 1 – Warning 2 – Electrical trip 3 – Shutdown 4 – Notification | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | Chrg Alt Threshold (volt) | 0 | 35 | 4 |  | float | volt | Pass | Sahil Sheikh | 2024-03-26
|  |  | Chrg Alt Delay (sec) | 5 | 60 | 60 |  | uint16 | sec | Pass | Sahil Sheikh | 2024-03-26
Preheat
|  |  | Preheat Timer (sec) | 1 | 900 | 2 |  | uint16 | sec | Pass | Sahil Sheikh | 2024-03-26
|  |  | Engine Temperature Limit |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | Engine Temperature Limit (°C) | -5 | 300 | 25 |  | uint16 | °C | Pass | Sahil Sheikh | 2024-03-26
|  |  | Ambient Temp |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
Engine Control Unit (ECU)
|  |  | Engine Type |  |  | 0 | 0-Conventional 1-ECU 162 | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | Lube Oil Pressure |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | Coolant Temperature |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | Engine Speed |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | Running Hours |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | Battery voltage |  |  | 0 | 0-Disable 1- Enable |  | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | Oil Temperature |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | ECU Communication ure Action (opt 5) |  |  | 0 | 0 – None 1 – Warning 2 – Electrical trip 3 – Shutdown 4 – Notification | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | ECU Communication ure Activation (opt 4) |  |  | 0 | 0 – Never 1 – From Engine start 2 – From monitoring On 3 – Always | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | ECU Communication Failure Activation Delay | 0 | 60 | 1 |  | uint8 | sec | Pass | Sahil Sheikh | 2024-03-26
|  |  | ECU Amber Lamp Action |  |  | 0 | 0 – None 1 – Warning 2 – Electrical trip 3 – Shutdown 4 – Notification | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | ECU Amber Lamp Activation |  |  | 0 | 0 – Never 1 – From Engine start 2 – From monitoring On 3 – Always | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | ECU Amber Lamp Activation Delay | 0 | 60 | 0 |  | uint8 | sec | Pass | Sahil Sheikh | 2024-03-26
|  |  | ECU Red Lamp Action |  |  | 0 | 0 – None 1 – Warning 2 – Electrical trip 3 – Shutdown 4 – Notification | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | ECU Red Lamp Activation |  |  | 0 | 0 – Never 1 – From Engine start 2 – From monitoring On 3 – Always | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | ECU Red Lamp Activation Delay | 0 | 60 | 0 |  | uint8 | sec | Pass | Sahil Sheikh | 2024-03-26
|  |  | ECU Malfunction Lamp Action |  |  | 0 | 0 – None 1 – Warning 2 – Electrical trip 3 – Shutdown 4 – Notification | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | ECU Malfunction Lamp Activation |  |  | 0 | 0 – Never 1 – From Engine start 2 – From monitoring On 3 – Always | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | ECU Malfunction Lamp Activation Delay | 0 | 60 | 0 |  | uint8 | sec | Pass | Sahil Sheikh | 2024-03-26
|  |  | ECU Protect Lamp Action |  |  | 0 | 0 – None 1 – Warning 2 – Electrical trip 3 – Shutdown 4 – Notification | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | ECU Protect Lamp Activation |  |  | 0 | 0 – Never 1 – From Engine start 2 – From monitoring On 3 – Always | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | ECU Protect Lamp Activation Delay | 0 | 60 | 60 |  | uint8 | sec | Pass | Sahil Sheikh | 2024-03-26
|  |  | GCU Source Address | 0 | 253 | 3 |  | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | ECU Source Address | 0 | 253 | 0 |  | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
Lube Oil Pressure
|  |  | Low Level Shutdown |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | Pass | Sangeet Wankhede | 2024-06-18
|  |  | Shutdown Threshold (bar) | 0 | 4.8 | 2 |  | float | bar | Pass | Sangeet Wankhede | 2024-06-18
|  |  | Low Level Warning |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | Pass | Sangeet Wankhede | 2024-06-18
|  |  | Warning Threshold (bar) | 0.2 | 5 | 3 |  | float | bar | Pass | Sangeet Wankhede | 2024-06-18
Coolant Temperature
|  |  | High Temp Shutdown |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | Shutdown Threshold (deg C) | 26 | 200 | 27 |  | float | °C | Pass | Sahil Sheikh | 2024-03-26
|  |  | High Temp Warning |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | Warning Threshold (deg C) | 25 | 199 | 25 |  | float | °C | Pass | Sahil Sheikh | 2024-03-26
Oil Temperature
|  |  | High Temp Shutdown |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | Shutdown Threshold (deg C) | 26 | 200 | 27 |  | float | °C | Pass | Sahil Sheikh | 2024-03-26
|  |  | High Temp Warning |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | Warning Threshold (deg C) | 25 | 199 | 25 |  | float | °C | Pass | Sahil Sheikh | 2024-03-26
|  | SPN Set | Engine Exhst O2 Sen Closed Loop Oper |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | NOT tested in this build | NA | NA
|  |  | ECU Temperature |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | NOT tested in this build | NA | NA
|  |  | Engine Intake Mainfold 1 Pressure |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | NOT tested in this build | NA | NA
|  |  | Engine Intake Mainfold 1 Temperature |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | NOT tested in this build | NA | NA
|  |  | Engine Exhaust Temperature |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | NOT tested in this build | NA | NA
|  |  | Key Switch Battery Potential |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | NOT tested in this build | NA | NA
|  |  | Engine Throttle Valve 1 Position 1 |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | NOT tested in this build | NA | NA
|  |  | Eng Protection Sys has Shutdown Eng |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | NOT tested in this build | NA | NA
|  |  | WWDM4 PGN 65453 SPN SET |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | NOT tested in this build | NA | NA
|  |  | Engine Fuel Valve 1 Position |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | NOT tested in this build | NA | NA
|  |  | Engine Throttle Valve 1 Differential Pressure |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | NOT tested in this build | NA | NA
|  |  | Engine Fuel Valve 1 Differential Pressure |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | NOT tested in this build | NA | NA
|  |  | Fuel Level 1 |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | NOT tested in this build | NA | NA
|  |  | Charging Sys Potential |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | NOT tested in this build | NA | NA
|  |  | Crank Attempts |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | NOT tested in this build | NA | NA
|  |  | Actuator Rack Position |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | NOT tested in this build | NA | NA
|  |  | Actuator Current |  |  | 0 | 0-Disable 1- Enable | uint8 | NA | NOT tested in this build | NA | NA
| Maintenance | Filter | Alarm Action (opt 2) |  |  | 0 | 0-Notification 1-Warning | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | Due At Engine Hours | 10 | 65000 | 250 |  | uint16 | Hrs | Pass | Sahil Sheikh | 2024-03-26
|  | keep current date + 3 months | Alarm Due Day | 1 | 31 | 6 |  | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | Alarm Due Month | 1 | 12 | 3 |  | uint8 | NA | Pass | Sahil Sheikh | 2024-03-26
|  |  | Alarm Due Year | 2024 | 2080 | 2024 |  | uint16 | NA | Pass | Sahil Sheikh | 2024-03-26

## NEW Ranges
SEDEMAC |  | Test Report For : SW-GC2X-GC2115-RA6M2 | [6 empty] | Doc # | SW-TEST_GC2X-GC2115-RA6M2
[9 empty] | Rev #/ Rev Date | 0.27/21 June 2024
[9 empty] | Page # | 7 of 24
FOR reference /DO NOT TEST | To compare with Old Firmware Ranges & dropdown list
Updated on 01-Feb-2024 | Documents ref link |  | https://sedemac.sharepoint.com/:x:/s/ProductLineGCU-GCUandB12ProductDevelopment/EezT3z2vzR9Eo3vAqr8r0P8BZxRetU67BfPMkjeLQ-HW7g?e=hPH2kS
Ranges for GC2115 and GC2116
| MODULE | SubMenu | Parameter Name | Min | Max | Default value | Units | Pass/Fail | Tested By | Date
Module
General
|  |  | Profile Name |  |  | Profile 1 | NA
|  |  | Power On Mode |  |  | 0 | NA
|  |  | Power On Lamp Test | Disable | Enable | 0 | NA
|  |  | Password Lock | NA | NA | 0 | NA
Display
|  |  | Display Contrast | 0 | 100 | 50 | %
|  |  | Power Save Mode | Disable | Enable | 0 | NA
|  | Modbus Communication | Comm Mode |  |  | 0 | NA
|  |  | MODBUS Slave ID | 1 | 247 | 2 | NA
|  |  | MODBUS Baudrate |  |  | 3 | NA
|  |  | Parity Bit |  |  | 0 | NA
|  | BTS | Battery Montoring | NO | YES | 1 | NA
|  |  | Low Battery Threshold | 40 | 55 | 46.5 | volt
|  |  | Low Battery Monitoring Delay | 5 | 300 | 10 | sec
|  |  | Genset Run Duration | 1 | 720 | 270 | min
|  | Cyclic Mode | Cyclic Mode | NO | YES | 0 | NA
|  |  | Genset Off Time | 1 | 720 | 240 | min
|  |  | Genset On Time | 1 | 720 | 240 | min
|  | Night Mode | Night Mode | Disable | Enable | 0 | NA
|  |  | Start Time | 0 | 23:59 | 9:59 | hrs.
|  |  | Off Duration | 1 | 1440 | 480 | min
|  | AUTO MD SWITCH | AUTO MD SWITCH | Disable | Enable | 0
|  |  | MANUAL MODE TIME (Min) | 16 | 120 | 16 | min
|  |  | OUTPUT ON TIME (Min) | 5 | 15 | 15 | min
Digital Inputs
Digital Input A
|  |  | Source |  |  | 0
|  |  | Polarity |  |  | 0
|  |  | Action |  |  | 0
|  |  | Activation |  |  | 2
|  |  | Activation Delay (Sec) | 1 | 180 | 1 | sec
Digital Input B
|  |  | Source |  |  | 0
|  |  | Polarity |  |  | 0
|  |  | Action |  |  | 0
|  |  | Activation |  |  | 2
|  |  | Activation Delay (Sec) | 1 | 180 | 1 | sec
Digital Input C
|  |  | Source |  |  | 0
|  |  | Polarity |  |  | 0
|  |  | Action |  |  | 0
|  |  | Activation |  |  | 2
|  |  | Activation Delay (Sec) | 1 | 180 | 1 | sec
Digital Input D
|  |  | Source |  |  | 0
|  |  | Polarity |  |  | 0
|  |  | Action |  |  | 0
|  |  | Activation |  |  | 2
|  |  | Activation Delay (Sec) | 1 | 180 | 1 | sec
Digital Input E
|  |  | Source |  |  | 0
|  |  | Polarity |  |  | 0
|  |  | Action |  |  | 0
|  |  | Activation |  |  | 2
|  |  | Activation Delay (Sec) | 1 | 180 | 1 | sec
Digital Input F
|  |  | Source |  |  | 0
|  |  | Polarity |  |  | 0
|  |  | Action |  |  | 0
|  |  | Activation |  |  | 2
|  |  | Activation Delay (Sec) | 1 | 180 | 1 | sec
Digital Input G
|  |  | Source |  |  | 0
|  |  | Polarity |  |  | 0
|  |  | Action |  |  | 0
|  |  | Activation |  |  | 2
|  |  | Activation Delay (Sec) | 1 | 180 | 1 | sec
Digital Input H
|  |  | Source |  |  | 0
|  |  | Polarity |  |  | 0
|  |  | Action |  |  | 0
|  |  | Activation |  |  | 2
|  |  | Activation Delay (Sec) | 1 | 180 | 1 | sec
Digital Input I
|  |  | Source |  |  | 0
|  |  | Polarity |  |  | 0
|  |  | Action |  |  | 0
|  |  | Activation |  |  | 2
|  |  | Activation Delay (Sec) | 1 | 180 | 1 | sec
Analog Inputs
LOP / DIG J
|  |  | Sensor Selection |  |  | 0
|  |  | Source |  |  | 0
|  |  | Polarity |  |  | 0
|  |  | Action |  |  | 0
|  |  | Activation |  |  | 2
|  |  | Activation Delay(Sec) | 1 | 180 | 1 | sec
|  |  | LOP Shutdown |  |  | 1
|  |  | LOP Shutdown threshold (bar) | 0 | 9.8 | 2 | bar
|  |  | LOP Warning |  |  | 1
|  |  | LOP Warning threshold (bar) | 0.2 | 10 | 3 | bar
|  |  | LOP Sensor Open Ckt Alarm |  |  | 0
|  |  | R1 | 0 | 1000 | 10 | ohm
|  |  | V1 | 0 | 10 | 0 | bar
|  |  | R2 | 0 | 1000 | 30 | ohm
|  |  | V2 | 0 | 10 | 1 | bar
|  |  | R3 | 0 | 1000 | 40 | ohm
|  |  | V3 | 0 | 10 | 2 | bar
|  |  | R4 | 0 | 1000 | 64 | ohm
|  |  | V4 | 0 | 10 | 3 | bar
|  |  | R5 | 0 | 1000 | 80 | ohm
|  |  | V5 | 0 | 10 | 4 | bar
|  |  | R6 | 0 | 1000 | 96 | ohm
|  |  | V6 | 0 | 10 | 5 | bar
|  |  | R7 | 0 | 1000 | 96 | ohm
|  |  | V7 | 0 | 10 | 5 | bar
|  |  | R8 | 0 | 1000 | 96 | ohm
|  |  | V8 | 0 | 10 | 5 | bar
|  |  | R9 | 0 | 1000 | 96 | ohm
|  |  | V9 | 0 | 10 | 5 | bar
|  |  | R10 | 0 | 1000 | 96 | ohm
|  |  | V10 | 0 | 10 | 5 | bar
Fuel Level / DIG K
|  |  | Sensor selection |  |  | 0
|  |  | Source |  |  | 0
|  |  | Polarity |  |  | 0
|  |  | Action |  |  | 0
|  |  | Activation |  |  | 2
|  |  | Activation Delay (Sec) | 1 | 180 | 1 | sec
|  | Fuel Level Monitoring | Low Fuel Level Shutdown |  |  | 1
|  |  | Low Fuel Level Shutdown threshold (%) | 0 | 78 | 10
|  |  | Low Fuel Level Notification |  |  | 1
|  |  | Low Fuel Level Notification threshold (%) | 2 | 80 | 12
|  |  | Fuel Tank Capacity (Litre) | 2 | 1000 | 100 | Litres
|  |  | Fuel Theft Warning |  |  | 1
|  |  | Fuel Theft Threshold (%/Hr) | 1 | 100 | 50 | %/Hr
|  |  | Fuel Consumption (Ltr/Hr) | 0 | 100 | 50 | Ltr/Hr
|  |  | Display Fuel In % |  |  | 0
|  |  | R1 | 0 | 1000 | 14 | ohm
|  |  | L1 | 0 | 100 | 0
|  |  | R2 | 0 | 1000 | 18 | ohm
|  |  | L2 | 0 | 100 | 5
|  |  | R3 | 0 | 1000 | 22 | ohm
|  |  | L3 | 0 | 100 | 10
|  |  | R4 | 0 | 1000 | 29 | ohm
|  |  | L4 | 0 | 100 | 15
|  |  | R5 | 0 | 1000 | 37 | ohm
|  |  | L5 | 0 | 100 | 20
|  |  | R6 | 0 | 1000 | 55 | ohm
|  |  | L6 | 0 | 100 | 25
|  |  | R7 | 0 | 1000 | 74 | ohm
|  |  | L7 | 0 | 100 | 30
|  |  | R8 | 0 | 1000 | 92 | ohm
|  |  | L8 | 0 | 100 | 35
|  |  | R9 | 0 | 1000 | 110 | ohm
|  |  | L9 | 0 | 100 | 40
|  |  | R10 | 0 | 1000 | 124 | ohm
|  |  | L10 | 0 | 100 | 45
|  |  | R11 | 0 | 1000 | 139 | ohm
|  |  | L11 | 0 | 100 | 50
|  |  | R12 | 0 | 1000 | 149 | ohm
|  |  | L12 | 0 | 100 | 55
|  |  | R13 | 0 | 1000 | 159 | ohm
|  |  | L13 | 0 | 100 | 60
|  |  | R14 | 0 | 1000 | 165 | ohm
|  |  | L14 | 0 | 100 | 65
|  |  | R15 | 0 | 1000 | 171 | ohm
|  |  | L15 | 0 | 100 | 70
|  |  | R16 | 0 | 1000 | 172 | ohm
|  |  | L16 | 0 | 100 | 75
|  |  | R17 | 0 | 1000 | 174 | ohm
|  |  | L17 | 0 | 100 | 80
|  |  | R18 | 0 | 1000 | 177 | ohm
|  |  | L18 | 0 | 100 | 85
|  |  | R19 | 0 | 1000 | 180 | ohm
|  |  | L19 | 0 | 100 | 90
|  |  | R20 | 0 | 1000 | 184 | ohm
|  |  | L20 | 0 | 100 | 100
Engine Temp / DIG L
|  |  | Sensor selection |  |  | 0
|  |  | Source |  |  | 0
|  |  | Polarity |  |  | 0
|  |  | Action |  |  | 0
|  |  | Activation |  |  | 2
|  |  | Activation Delay (Sec) | 1 | 180 | 1 | Sec
|  | Temp Sensor | High Temp. Action |  |  | 0
|  |  | High temp. threshold | 25 | 300 | 25
|  |  | Engine Temp Open Ckt Alarm |  |  | 0
|  |  | R1 | 0 | 5000 | 35 | ohm
|  |  | T1 | -5 | 300 | 125 | °C
|  |  | R2 | 0 | 5000 | 50 | ohm
|  |  | T2 | -5 | 300 | 110 | °C
|  |  | R3 | 0 | 5000 | 70 | ohm
|  |  | T3 | -5 | 300 | 100 | °C
|  |  | R4 | 0 | 5000 | 93 | ohm
|  |  | T4 | -5 | 300 | 90 | °C
|  |  | R5 | 0 | 5000 | 120 | ohm
|  |  | T5 | -5 | 300 | 85 | °C
|  |  | R6 | 0 | 5000 | 220 | ohm
|  |  | T6 | -5 | 300 | 65 | °C
|  |  | R7 | 0 | 5000 | 458 | ohm
|  |  | T7 | -5 | 300 | 45 | °C
|  |  | R8 | 0 | 5000 | 700 | ohm
|  |  | T8 | -5 | 300 | 35 | °C
|  |  | R9 | 0 | 5000 | 850 | ohm
|  |  | T9 | -5 | 300 | 35 | °C
|  |  | R10 | 0 | 5000 | 1000 | ohm
|  |  | T10 | -5 | 300 | 35 | °C
Shelter Temp Sensor / Dig M
|  |  | Sensor Selection |  |  | 0
|  |  | Source |  |  | 0
|  |  | Polarity |  |  | 0
|  |  | Action |  |  | 0
|  |  | Activation |  |  | 2
|  |  | Activation Delay(Sec) | 1 | 180 | 1 | Sec
|  | Shelter Sensor Monitoring | High Temp Threshold | 20 | 60 | 60 | °C
|  |  | Low Temp Threshold | 18 | 55 | 55 | °C
|  |  | Shelt Temp Monitoring Delay(Sec) | 5 | 300 | 10 | Sec
|  |  | Shelt Temp Run Duration | 1 | 720 | 2 | min
|  |  | Circuit fault notification |  |  | 0
|  |  | R1 | 0 | 1000 | 1000 | ohm
|  |  | Val1 | -5 | 300 | 15 | °C
|  |  | R2 | 0 | 1000 | 841 | ohm
|  |  | Val2 | -5 | 300 | 20 | °C
|  |  | R3 | 0 | 1000 | 680 | ohm
|  |  | Val3 | -5 | 300 | 25 | °C
|  |  | R4 | 0 | 1000 | 554 | ohm
|  |  | Val4 | -5 | 300 | 30 | °C
|  |  | R5 | 0 | 1000 | 374 | ohm
|  |  | Val5 | -5 | 300 | 40 | °C
|  |  | R6 | 0 | 1000 | 311 | ohm
|  |  | Val6 | -5 | 300 | 45 | °C
|  |  | R7 | 0 | 1000 | 259 | ohm
|  |  | Val7 | -5 | 300 | 50 | °C
|  |  | R8 | 0 | 1000 | 218 | ohm
|  |  | Val8 | -5 | 300 | 55 | °C
|  |  | R9 | 0 | 1000 | 183 | ohm
|  |  | Val9 | -5 | 300 | 60 | °C
|  |  | R10 | 0 | 1000 | 156 | ohm
|  |  | Val10 | -5 | 300 | 65 | °C
S2 SENSOR / Dig N
|  |  | Sensor Selection |  |  | 0
|  |  | Source |  |  | 0
|  |  | Polarity |  |  | 0
|  |  | Action |  |  | 0
|  |  | Activation |  |  | 2
|  |  | Activation Delay(Sec) | 1 | 180 | 1 | Sec
|  | S2 SENSOR MONITORING | Action |  |  | 0
|  |  | Threshold | 0 | 1000 | 100
|  |  | Threshold Type |  |  | 0
|  |  | Sensor / Alarm name |  |  | S2 sensor
|  |  | R1 | 0 | 1000 | 0
|  |  | Val1 | 0 | 1000 | 0
|  |  | R2 | 0 | 1000 | 0
|  |  | Val2 | 0 | 1000 | 0
|  |  | R3 | 0 | 1000 | 0
|  |  | Val3 | 0 | 1000 | 0
|  |  | R4 | 0 | 1000 | 0
|  |  | Val4 | 0 | 1000 | 0
|  |  | R5 | 0 | 1000 | 0
|  |  | Val5 | 0 | 1000 | 0
|  |  | R6 | 0 | 1000 | 0
|  |  | Val6 | 0 | 1000 | 0
|  |  | R7 | 0 | 1000 | 0
|  |  | Val7 | 0 | 1000 | 0
|  |  | R8 | 0 | 1000 | 0
|  |  | Val8 | 0 | 1000 | 0
|  |  | R9 | 0 | 1000 | 0
|  |  | Val9 | 0 | 1000 | 0
|  |  | R10 | 0 | 1000 | 0
|  |  | Val10 | 0 | 1000 | 0
S3 SENSOR / Dig O
|  |  | Sensor Selection |  |  | 0
|  |  | Source |  |  | 0
|  |  | Polarity |  |  | 0
|  |  | Action |  |  | 0
|  |  | Activation |  |  | 2
|  |  | Activation Delay(Sec) | 1 | 180 | 1 | sec
|  | LOP (4-20mA) | LOP Shutdown (4-20mA) |  |  | 0
|  |  | LOP Shutdown threshold (bar) | 0 | 9.8 | 2 | bar
|  |  | LOP Warning |  |  | 0
|  |  | LOP Warning threshold (bar) | 0.2 | 10 | 3 | bar
|  |  | Circuit Fault Action |  |  | 0
|  |  | I1 | 4 | 20 | 4 | mA
|  |  | V1 | 0 | 10 | 0 | bar
|  |  | I2 | 4 | 20 | 6 | mA
|  |  | V2 | 0 | 10 | 1 | bar
|  |  | I3 | 4 | 20 | 7 | mA
|  |  | V3 | 0 | 10 | 2 | bar
|  |  | I4 | 4 | 20 | 9 | mA
|  |  | V4 | 0 | 10 | 3 | bar
|  |  | I5 | 4 | 20 | 10 | mA
|  |  | V5 | 0 | 10 | 4 | bar
|  |  | I6 | 4 | 20 | 12 | mA
|  |  | V6 | 0 | 10 | 5 | bar
|  |  | I7 | 4 | 20 | 14 | mA
|  |  | V7 | 0 | 10 | 6 | bar
|  |  | I8 | 4 | 20 | 15 | mA
|  |  | V8 | 0 | 10 | 7 | bar
|  |  | I9 | 4 | 20 | 17 | mA
|  |  | V9 | 0 | 10 | 8 | bar
|  |  | I10 | 4 | 20 | 20 | mA
|  |  | V10 | 0 | 10 | 10 | bar
|  | LOP(0-5V) | LOP Shutdown (0-5V) |  |  | 0
|  |  | LOP Shutdown threshold (bar) | 0 | 9.8 | 9.8 | bar
|  |  | LOP Warning |  |  | 0
|  |  | LOP Warning threshold (bar) | 0 | 10 | 10 | bar
|  |  | Circuit Fault Action |  |  | 0
|  |  | I1 | 0 | 5 | 0.5 | volts
|  |  | V1 | 0 | 10 | 0 | bar
|  |  | I2 | 0 | 5 | 0.9 | volts
|  |  | V2 | 0 | 10 | 1 | bar
|  |  | I3 | 0 | 5 | 1.3 | volts
|  |  | V3 | 0 | 10 | 2 | bar
|  |  | I4 | 0 | 5 | 1.7 | volts
|  |  | V4 | 0 | 10 | 3 | bar
|  |  | I5 | 0 | 5 | 2.1 | volts
|  |  | V5 | 0 | 10 | 4 | bar
|  |  | I6 | 0 | 5 | 2.5 | volts
|  |  | V6 | 0 | 10 | 5 | bar
|  |  | I7 | 0 | 5 | 2.9 | volts
|  |  | V7 | 0 | 10 | 6 | bar
|  |  | I8 | 0 | 5 | 3.3 | volts
|  |  | V8 | 0 | 10 | 7 | bar
|  |  | I9 | 0 | 5 | 3.7 | volts
|  |  | V9 | 0 | 10 | 8 | bar
|  |  | I10 | 0 | 5 | 4.5 | volts
|  |  | V10 | 0 | 10 | 10 | bar
S4 SENSOR / Dig P
|  |  | Sensor Selection |  |  | 0
|  |  | Source |  |  | 0
|  |  | Polarity |  |  | 0
|  |  | Action |  |  | 0
|  |  | Activation |  |  | 2
|  |  | Activation Delay(Sec) | 1 | 180 | 1 | sec
|  | Fuel Level Monitoring | Fuel Level Monitoring |  |  | 1
|  |  | Low Fuel Level Shutdown threshold (%) | 0 | 78 | 10 | %
|  |  | Low Fuel Level Notification |  |  | 1
|  |  | Low Fuel Level Notification threshold (%) | 2 | 80 | 12 | %
|  |  | Fuel Theft Alarm |  |  | 1
|  |  | Fuel Theft Threshold (%/Hr) | 1 | 100 | 50 | %/Hr
|  |  | Fuel Consumption (Ltr/Hr) | 0 | 100 | 50 | Ltr/Hr
|  |  | Display Fuel In Liters |  |  | 0
|  |  | Sensor Low Voltage (Volt) (2 decimal) | 0 | 5 | 0 | volt
|  |  | Sensor High Voltage (Volt) | 0 | 5 | 5 | volt
|  |  | Tank With Step |  |  | 1
|  |  | Tank Width (mm) - For Both Steps | 0 | 3000 | 600
|  |  | Tank Step 1 Length (mm) | 0 | 3000 | 1000 | mm
|  |  | Tank Step 1 Heigth (mm) | 0 | 3000 | 200 | mm
|  |  | Tank Step 2 Length (mm) | 0 | 3000 | 600 | mm
|  |  | Tank Step 2 Heigth (mm) | 0 | 3000 | 150 | mm
Outputs
Digital Output A
|  |  | Source |  |  | 0
|  |  | Polarity |  |  | 0
Digital Output B
|  |  | Source |  |  | 0
|  |  | Polarity |  |  | 0
Digital Output C
|  |  | Source |  |  | 0
|  |  | Polarity |  |  | 0
Digital Output D
|  |  | Source |  |  | 0
|  |  | Polarity |  |  | 0
Digital Output E
|  |  | Source |  |  | 0
|  |  | Polarity |  |  | 0
Digital Output F
|  |  | Source |  |  | 0
|  |  | Polarity |  |  | 0
Digital Output G
|  |  | Source |  |  | 0
|  |  | Polarity |  |  | 0
Timers
Cranking
|  |  | Crank Hold Time (sec) | 1 | 10 | 4 | sec
|  |  | Crank Rest Time (sec) | 2 | 60 | 10 | sec
|  |  | Manual Start Delay (sec) | 1 | 10 | 3 | sec
|  |  | Auto Start Delay (sec) | 1 | 10 | 5 | sec
General
|  |  | Safety Monotoring Delay (sec) | 10 | 60 | 10 | sec
|  |  | Mains Detect Delay (sec) | 1 | 30 | 5 | sec
|  |  | Alternator Detect Delay (sec) | 1 | 30 | 5 | sec
|  |  | Warm-up Delay (sec) | 10 | 60 | 30 | sec
|  |  | Return To Mains Delay (sec) | 0 | 600 | 60 | sec
|  |  | Engine Cooling Time (sec) | 59 | 300 | 60 | sec
|  |  | Stop Action Time (sec) | 10 | 120 | 30 | sec
|  |  | Additional Stopping Time (sec) | 0 | 120 | 10 | sec
|  |  | Load Transfer Delay (sec) | 1 | 60 | 5 | sec
|  |  | Power Save Mode Delay (sec) | 0 | 120 | 60 | sec
|  |  | Screen Changeover Time (sec) | 0 | 60 | 30 | sec
|  |  | Sounder Alarm Time (sec) | 1 | 300 | 60 | sec
|  |  | Test Mode Timer (min) | 1 | 720 | 1 | min
Generator
Alternator Config
|  |  | Alternator Present |  |  | 1
|  |  | Number of Poles (options 4) |  |  | 1
|  |  | AC System (opt 2) |  |  | 0
|  |  | Min Healthy Voltage (volt) | 180 | 270 | 185 | volt Ph-N
|  |  | Min Healthy Frequency (Hz) | 44 | 56 | 47 | Hz
|  |  | Phase Reversal Detection |  |  | 0
|  |  | Phase Reversal Action (opt 4) |  |  | 0
|  |  | Auto-load Transfer |  |  | 0
|  |  | Alternator Wave Detection |  |  | 0
Voltage Monitoring
|  |  | UV Shutdown Enable |  |  | 1
|  |  | UV Shutdown Threshold (volt) | 180 | 225 | 184 | volt Ph-N
|  |  | UV Warning Enable |  |  | 1
|  |  | UV Warning Threshold (volt) | 185 | 230 | 189 | volt Ph-N
|  |  | OV Shutdown Enable |  |  | 1
|  |  | OV Shutdown Threshold (volt) | 235 | 270 | 264 | volt Ph-N
|  |  | OV Warning Enable |  |  | 1
|  |  | OV Warning Threshold(volt) | 230 | 265 | 260 | volt Ph-N
Frequency Monitoring
|  |  | UF Shutdown Enable |  |  | 1
|  |  | UF Shutdown Threshold (Hz) | 44 | 48 | 47 | Hz
|  |  | UF Warning Enable |  |  | 1
|  |  | UF Warning Threshold (Hz) | 45 | 49 | 48 | Hz
|  |  | OF Shutdown Enable |  |  | 1
|  |  | OF Shutdown Threshold (Hz) | 52 | 56 | 53 | Hz
|  |  | OF Warning Enable |  |  | 1
|  |  | OF Warning Threshold (Hz) | 51 | 55 | 52 | Hz
Current monitoring
|  |  | CT Ratio | 0 | 8000 | 100
|  |  | Over-current Action (opt 4) |  |  | 3
|  |  | Over-current Threshold (Amp) | 5 | 10000 | 44 | Amp
|  |  | Over-current Delay (sec) | 1 | 600 | 3 | sec
|  |  | CT Correction Factor | 0.9 | 1.1 | 1
|  |  | CT Location |  |  | 1
Fan Current Monitoring
|  |  | Monitoring Enable |  |  | 1
|  |  | Fan CT Ratio | 0 | 8000 | 0
|  |  | Fan Current High Threshold | 0.1 | 10 | 0.2 | Amp
|  |  | Fan Current High Action (5 options) |  |  | 0
|  |  | Fan Current Low Threshold | 0 | 9.9 | 0 | Amp
|  |  | Fan Current Low Action (opt 5) |  |  | 0
|  |  | Fan Current Delay (sec) | 1 | 180 | 1 | sec
Load Monitoring
|  |  | Generator Rating (kW) | 0 | 800 | 8 | kw
|  |  | Full Load Current (Amp/Phase) | 1 | 800 | 1 | Amp/Phase
|  |  | Over-load Action (opt 4) |  |  | 3
|  |  | Load Monitoring Threshold (%) | 100 | 150 | 111 | %
|  |  | Over-load Delay (sec) | 1 | 60 | 3 | sec
|  |  | Unbalanced Load Action |  |  | 0
|  |  | Unbalanced Load Threshold (%) | 5 | 100 | 25 | %
|  |  | Unbalanced Load Delay (sec) | 1 | 60 | 10 | sec
|  |  | Unbalanced Load Activation Threshold (%) | 0 | 100 | 60 | %
Mains
Mains Config
|  |  | Mains Monitoring |  |  | 1
|  |  | Mains AC system (opt 2) |  |  | 1
|  |  | Phase Reversal Detection |  |  | 0
|  |  | Phase Reversal Action (opt 2) |  |  | 0
|  |  | Three Phase calc for one phase |  |  | 1
Under-voltage Monitoring
|  |  | Monitoring Enable |  |  | 1
|  |  | Under-voltage Trip (Volt) | 99 | 240 | 122 | volt Ph-N
|  |  | Under-voltage Return (Volt) | 122 | 242 | 131 | volt Ph-N
Over-voltage Monitoring
|  |  | Monitoring Enable |  |  | 1
|  |  | Over-voltage Trip (Volt) | 202 | 288 | 287 | volt Ph-N
|  |  | Over-voltage Return (Volt) | 200 | 286 | 277 | volt Ph-N
Under-frequency Monitoring
|  |  | Monitoring Enable |  |  | 1
|  |  | Under-frequency Trip (Hz) | 40 | 48 | 45 | Hz
|  |  | Under-frequency Return (Hz) | 41 | 49 | 46 | Hz
Over-frequency Monitoring
|  |  | Monitoring Enable |  |  | 1
|  |  | Over-frequency Trip (Hz) | 52 | 60 | 54 | Hz
|  |  | Over-frequency Return (Hz) | 51 | 59 | 53 | Hz
Engine
Crank Disconnect
|  |  | Start Attempts | 1 | 10 | 3
|  |  | Disconnect On LOP Sensor |  |  | 0
|  |  | Disconnect Pressure Threshold (bar) | 0.5 | 10 | 4 | bar
|  |  | Mon Pres Switch Before Start |  |  | 0
|  |  | Mon Pres Sensor Before Start |  |  | 0
|  |  | Disconnect On LLOP Switch |  |  | 0
|  |  | LLOP Switch Transient Time (sec) | 0 | 3 | 0.1 | sec
|  |  | Alternator Frequency (Hz) | 10 | 25 | 20 | Hz
|  |  | Engine Speed (Speed) | 150 | 800 | 600 | rpm
|  |  | Disconnect On Charging Alt Voltage |  |  | 0
|  |  | Charging Alt Voltage Threshold | 5 | 30 | 8 | volt
Speed Monitoring
|  |  | Engine Speed Sense Source (opt 1) |  |  | 0
|  |  | Under-speed Shutdown |  |  | 1
|  |  | Under-speed Threshold (RPM) | 1300 | 1500 | 1380 | rpm
|  |  | Under-speed Delay (sec) | 1 | 60 | 10 | sec
|  |  | Over-speed Threshold (RPM) | 1500 | 1680 | 1650 | rpm
|  |  | Over-speed Delay (sec) | 1 | 20 | 10 | sec
|  |  | Gross Over-speed Threshold (%) | 100 | 200 | 120 | %
Battery Monitoring
|  |  | Low Battery voltage action |  |  | 4
|  |  | Low Battery Voltage Threshold (volt) | 8 | 12 | 10 | volt
|  |  | Low Battery Voltage Delay (sec) | 5 | 1800 | 60 | sec
|  |  | High Battery Voltage Action |  |  | 1
|  |  | High Battery Voltage Threshold (volt) | 12 | 17 | 14 | volt
|  |  | High Battery Voltage Delay (sec) | 5 | 1800 | 30 | sec
Charging Alt Monitoring
|  |  | Charging Alt Action (opt 5) |  |  | 4
|  |  | Chrg Alt Threshold (volt) | 0 | 35 | 4 | volt
|  |  | Chrg Alt Delay (sec) | 5 | 60 | 60 | sec
Preheat
|  |  | Preheat Timer (sec) | 1 | 900 | 2 | sec
|  |  | Engine Temperature Limit |  |  | 0
|  |  | Engine Temperature Limit (°C) | 10 | 300 | 25 | °C
|  |  | Ambient Temp |  |  | 0
Engine Control Unit (ECU)
|  |  | Engine Type |  |  | 0
Measurements From ECU
|  |  | Lube Oil Pressure |  |  | 0
|  |  | Coolant Temperature |  |  | 0
|  |  | Engine Speed |  |  | 0
|  |  | Running Hours |  |  | 0
|  |  | Battery voltage |  |  | 0
|  |  | Oil Temperature |  |  | 0
Communication
|  |  | ECU Communication ure Action (opt 5) |  |  | 0
|  |  | ECU Communication ure Activation (opt 4) |  |  | 0
|  |  | ECU Communication ure Activation Delay | 1 | 60 | 1 | sec
ECU Diagnostic Lamps
|  |  | ECU Amber Lamp Action |  |  | 0
|  |  | ECU Amber Lamp Activation |  |  | 0
|  |  | ECU Amber Lamp Activation Delay | 0 | 60 | 0 | sec
|  |  | ECU Red Lamp Action |  |  | 0
|  |  | ECU Red Lamp Activation |  |  | 0
|  |  | ECU Red Lamp Activation Delay | 0 | 60 | 0 | sec
|  |  | ECU Malfunction Lamp Action |  |  | 0
|  |  | ECU Malfunction Lamp Activation |  |  | 0
|  |  | ECU Malfunction Lamp Activation Delay | 0 | 60 | 0 | sec
|  |  | ECU Protect Lamp Action |  |  | 0
|  |  | ECU Protect Lamp Activation |  |  | 0
|  |  | ECU Protect Lamp Activation Delay | 0 | 60 | 60 | sec
|  |  | GCU Source Address | 0 | 253 | 3
|  |  | ECU Source Address | 0 | 253 | 0
Lube Oil Pressure
|  |  | Low Level Shutdown |  |  | 0
|  |  | Shutdown Threshold (bar) | 0 | 4.8 | 2 | bar
|  |  | Low Level Warning |  |  | 0
|  |  | Warning Threshold (bar) | 0.2 | 5 | 3 | bar
Coolant Temperature
|  |  | High Temp Shutdown |  |  | 0
|  |  | Shutdown Threshold (deg C) | 26 | 200 | 27 | °C
|  |  | High Temp Warning |  |  | 0
|  |  | Warning Threshold (deg C) | 25 | 199 | 25 | °C
Oil Temperature
|  |  | High Temp Shutdown |  |  | 0
|  |  | Shutdown Threshold (deg C) | 26 | 200 | 27 | °C
|  |  | High Temp Warning |  |  | 0
|  |  | Warning Threshold (deg C) | 25 | 199 | 25 | °C
| Maintenance | Filter | Alarm Action (opt 2) |  |  | 0
|  |  | Due At Engine Hours | 10 | 65000 | 250 | Hrs
|  | keep current date + 3 months | Alarm Due Day | 1 | 31 | 6
|  |  | Alarm Due Month | 1 | 12 | 3
|  |  | Alarm Due Year | 2024 | 2080 | 2024

## GCU Site Data Update Tool v1.0
SEDEMAC |  | Test Report For : SW-GC2X-GC2115-RA6M2 | [6 empty] | Doc # | SW-TEST_GC2X-GC2115-RA6M2
[9 empty] | Rev #/ Rev Date | 0.27/21 June 2024
[9 empty] | Page # | 8 of 24
Compatible Product Revision: GC2115R1, GC2116R1, GC2117R1
FOR Reference only Not for testing
GCU Site Data Update Tool v1.0
The tool will be called “GCU Site Data Update Tool”. It will be a separate tool different from Smart Config-R. On opening, it will ask for password. If the password entered is incorrect, the application will exit, If the password is correct, a new form will open which will allow user to edit 5 variables (given in table below).
There will be 2 buttons along with the text boxes: ‘Read’ button and ‘Write’ button. Both of them will be disabled until ‘GC2115 R1’ or ‘GC2116 R1’ (or any future product/revision in the Rjio series) is connected. When the compatible device is connected, a message would be displayed at bottom ‘XYZ device is connected’ and both buttons would be enabled. The read button would allow user to read the 5 variables from the GCU and write button would allow them to flash them at given addresses.
| Sr. No. | Test Case ID | Description | Module/ Functionality under test | Corresponding SRS ID | Expected result | Actual result Firmware Detials & Utility Version details | Pass/Fail | Tested by | Date of testing
| 1 |  | Executable set up file "GCU Site Data Update Tool.exe" should get properly installed on the computer with Windows 8/10/11 platform | Installation |  | As described
| 2 |  | After double click it should run the utility and seperate window should pop up requesting password in order to enter into utility | Run |  | As described
| 3 | Password | While opening using the password “2025” a Separate ID flashing UI will open and User will enter the required data and Click on Flash. similarly, we need a Read button, so existing flashed data will be read from GCU. | Password |  | As described
| 4 |  | Need to Write below data using tool:
|  |  | Genset Serial No -Max 19 characters (null-terminated) | Writing
Engine Serial No -Max 19 characters (null-terminated)
Alternator Serial No -Max 19 characters (null-terminated)
Engine Controller Serial No -Max 19 characters (null-terminated)
SITE ID -Max 19 characters (null-terminated). But only the first 9 characters are shown if it's length exceeds 9 character.

## NEW Dropdownlists
SEDEMAC |  | Test Report For : SW-GC2X-GC2115-RA6M2 | [5 empty] | Doc # | SW-TEST_GC2X-GC2115-RA6M2
[8 empty] | Rev #/ Rev Date | 0.27/21 June 2024
[8 empty] | Page # | 9 of 24
Updated on 01-Feb-2024 |  | Documents ref link | https://sedemac.sharepoint.com/:x:/s/ProductLineGCU/EdrWJtBvETFBpwMqU1Vg7asBfLi5O4Zn34jHBRh8fENPLA?e=I2Uc0x
| MODULE | SubMenu | Parameter # | Observed results | Pass/Failed | Tested By | Date
| ENGINE | Engine Name | Enum
|  | ENG_CONVENTIONAL | 0 |  | Pass | Sahil Sheikh | 2024-03-26
|  | ECU162 | 1 |  | Pass | Sahil Sheikh | 2024-03-26
| INPUTS | Digital Input Source | Enum
|  | Not Used | 0 |  | Pass | Sahil Sheikh | 2024-03-26
|  | User Configured | 1 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Low Fuel LVL Switch | 2 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Low Lube Oil Press Switch | 3 |  | Pass | Sahil Sheikh | 2024-03-26
|  | High Engine Temp Switch | 4 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Low Water LVL Switch | 5 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Emergency Stop | 6 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Remote Start / Stop | 7 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Simulate Start | 8 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Simulate Stop | 9 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Simulate Auto | 10 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Close Gen/Open Mains SW | 11 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Close Mains/Open Gen SW | 12 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Simulate Mains | 13 |  | Pass | Sahil Sheikh | 2024-03-26
|  | V-Belt Broken Switch | 14 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Mains Contactor Latched | 15 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Genset Contactor Latched | 16 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Battery Charger | 17 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Smoke Fire | 18 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Mode Select Switch | 19 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Ambient Temp Switch | 20 |  | Pass | Sahil Sheikh | 2024-03-26
|  | EGR Digital In | 21 |  | Pass | Sahil Sheikh | 2024-03-26
|  | EB MCCB On Feedback | 22 |  | Pass | Sahil Sheikh | 2024-03-26
|  | DG MCCB On Feedback | 23 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Supercapacitor Fail | 24 |  | Pass | Sahil Sheikh | 2024-03-26
| OUTPUTS | Digital Output Source | Enum
|  | Disable | 0 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Sounder Alarm | 1 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Battery Over Volt | 2 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Battery Under Volt | 3 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Charge Alt Shutdown | 4 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Charge Alt Warning | 5 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Close Gen Contactor | 6 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Close Mains Contactor | 7 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Mains Failure | 8 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Common Alarm | 9 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Common Electrical Trip | 10 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Common Shutdown | 11 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Common Warning | 12 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Cooling Down | 13 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Dig In A | 14 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Dig In B | 15 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Dig In C | 16 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Dig In D | 17 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Dig In E | 18 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Dig In F | 19 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Dig In G | 20 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Dig In H | 21 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Dig In I | 22 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Dig In J (LOP Resistive) | 23 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Dig In K (Anlg In Fuel LVL) | 24 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Dig In L (Anlg In Eng Temp) | 25 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Dig In M (Aux Sensor 1) | 26 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Dig In N (Aux Sensor 2) | 27 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Dig In O (Aux Sensor 3) | 28 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Dig In P (Aux Sensor 4) | 29 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Emergency Stop | 30 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Stop Solenoid | 31 |  | Pass | Sahil Sheikh | 2024-03-26
|  | To Start | 32 |  | Pass | Sahil Sheikh | 2024-03-26
|  | To Stop | 33 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Fuel Relay | 34 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Gen Available | 35 |  | Pass | Sahil Sheikh | 2024-03-26
|  | R Phase OV Shutdown | 36 |  | Pass | Sahil Sheikh | 2024-03-26
|  | R Phase UV Shutdown | 37 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Y Phase OV Shutdown | 38 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Y Phase UV Shutdown | 39 |  | Pass | Sahil Sheikh | 2024-03-26
|  | B Phase OV Shutdown | 40 |  | Pass | Sahil Sheikh | 2024-03-26
|  | B Phase UV Shutdown | 41 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Gen Over Current | 42 |  | Pass | Sahil Sheikh | 2024-03-26
|  | High Engine Temp | 43 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Low Fuel LVL | 44 |  | Pass | Sahil Sheikh | 2024-03-26
|  | LFL Sensor Notification | 45 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Low LOP | 46 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Mains High Volt | 47 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Mains Low Volt | 48 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Pressure Open Circuit | 49 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Open Gen Contactor | 50 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Open Mains Contactor | 51 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Over Freq Shutdown | 52 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Over Speed Shutdown | 53 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Gross Over Spd Shutdown | 54 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Start Relay | 55 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Temp Sensor Open Circuit | 56 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Under Freq Shutdown | 57 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Under Speed Shutdown | 58 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Maintenance Due | 59 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Stop Mode | 60 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Auto Mode | 61 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Manual Mode | 62 |  | Pass | Sahil Sheikh | 2024-03-26
|  | BTS Mode | 63 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Preheat Output | 64 |  | Pass | Sahil Sheikh | 2024-03-26
|  | ECU Start | 65 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Malfunction Indicator Lamp | 66 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Inducement Buzzer | 67 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Dig In Q | 68 |  | Pass | Sahil Sheikh | 2024-03-26
|  | Dig In R | 69 |  | Pass | Sahil Sheikh | 2024-03-26

## Geset Data set for CANJ1939
SEDEMAC |  | Test Report For : SW-GC2X-GC2115-RA6M2 | [6 empty] | Doc # | SW-TEST_GC2X-GC2115-RA6M2
[9 empty] | Rev #/ Rev Date | 0.27/21 June 2024
[9 empty] | Page # | 10 of 24
Original sheet reference GC1114 ECU162 DTC list on Microsoft Teams:
Sr No | J1939 PGN |  | SPN |  | Bit map | Actual result | Pass/ Failed | Tested by | Date of testing
| PGN | Name | Name | SPN
1 | 64911 | Generator Total AC Percent Power | Generator Total Percent kW | 3590 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
2 | 65008 | Mains Phase B AC Basic Quantities | Mains Phase BR Line-Line AC RMS Voltage | 2477 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Mains Phase B Line-Neutral AC RMS Voltage | 2481 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Mains Phase B AC Frequency | 2473 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
3 | 65011 | Mains Phase Y AC Basic Quantities | Mains Phase YB Line-Line AC RMS Voltage | 2476 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Mains Phase Y Line-Neutral AC RMS Voltage | 2480 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Mains Phase Y AC Frequency | 2472 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
4 | 65014 | Mains Phase R Basic AC Quantities | Mains Phase RY Line-Line AC RMS Voltage | 2475 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Mains Phase R Line-Neutral AC RMS Voltage | 2479 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Mains Phase R AC Frequency | 2471 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
5 | 65018 | Genset total RB energy | Generator total kW hours | 2468 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
6 | 65019 | Generator Phase B AC Reactive Power | Generator Phase B Reactive Power | 2459 | As per J1939
|  |  | Generator Phase B Power Factor | 2467 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
7 | 65020 | Generator Phase B AC Power | Generator Phase B Real Power | 2455 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Generator Phase B Apparent Power | 2463 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
8 | 65021 | Generator Phase B Basic AC Quantities | Generator Phase BR Line- Line AC RMS Voltage | 2443 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Generator Phase B Line- Neutral AC RMS Voltage | 2447 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Generator Phase B AC Frequency | 2439 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Generator Phase B AC RMS Current | 2451 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
9 | 65022 | Generator Phase Y AC Reactive Power | Generator Phase Y Reactive Power | 2458 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Generator Phase Y Power Factor | 2466 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
10 | 65023 | Generator Phase Y AC Power | Generator Phase Y Real Power | 2454 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Generator Phase Y Apparent Power | 2462 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
11 | 65024 | Generator Phase Y Basic AC Quantities | Generator Phase YB Line-Line AC RMS Voltage | 2442 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Generator Phase Y Line- Neutral AC RMS Voltage | 2446 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Generator Phase Y AC Frequency | 2438 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Generator Phase Y AC RMS Current | 2450 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
12 | 65025 | Generator Phase R AC Reactive Power | Generator Phase R Reactive Power | 2457 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Generator Phase R Power Factor | 2465 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
13 | 65026 | Generator Phase R AC Power | Generator Phase R Real Power | 2453 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Generator Phase R Apparent Power | 2461 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
14 | 65027 | Generator Phase R Basic AC Quantities | Generator Phase RY Line- Line AC RMS Voltage | 2441 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Generator Phase R Line- Neutral AC RMS Voltage | 2445 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Generator Phase R AC Frequency | 2437 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Generator Phase R AC RMS Current | 2449 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
15 | 65028 | Generator Total AC Reactive Power | Generator Total Reactive Power | 2456 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Generator Overall Power Factor | 2464 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
16 | 65029 | Generator Total AC Power | Generator Total Real Power | 2452 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Generator Total Apparent Power | 2460 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
17 | 65030 | Generator Average Basic AC Quantities | Generator Average Line-Line AC RMS Voltage | 2440 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Generator Average Line- Neutral AC RMS Voltage | 2444 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Generator Average AC Frequency | 2436 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Generator Average AC RMS Current | 2448 | As per J1939 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
Sr No | PGN | Description | SPN Description | Byte mapping | Bit map
18 | 65280 | SEDEMAC_Prop_B_2 | Sedemac mode: SEDEMAC Mode | Byte 0 | 0-1 bits (0- Manual engine off 1- Auto mode 2-Manual engine on 3-Other than above mode (Config Mode) ) | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Reserved |  | 2-7 bits | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Reserved 1 | Byte 1-2 | Byte 1-2 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Min healthy frequency | Byte 3 | Byte 3 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Min healthy voltage | Byte 4-5 | Byte 4-5
|  |  | Reserved 2 | Byte 6-7 | Byte 6-7 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
19 | 65289 | Prop Bit Fields 1 | Digital input a | 8-15 byte 1 | 15 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Digital input b |  | 14 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Digital input c |  | 13 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Digital input d |  | 12 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Digital input e |  | 11 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Digital input f |  | 10 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Digital input g |  | 9
|  |  | Digital input h |  | 8 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Digital output a | 0-7 byte 0 | 7 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Digital output b |  | 6 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Digital output c |  | 5 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Digital output d |  | 4 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Digital output e |  | 3 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Digital output f |  | 2 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Unimplemented |  | 1 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Unimplemented |  | 0 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | GCU Mode | Byte 3 | 31(Auto 0 /Manual 1) | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Mains Healthy / unhealthy |  | 30 (healthy 0 / unhealthy 1) | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Genset operation mode |  | 27-29(Auto- 101 Manual-100 Reserved) | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Load on Mains |  | 26 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Load on Genset |  | 25 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Current Genset status |  | 24(0- Stopped 1- Running ) | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Genset stopped normally | Byte 2 | 23 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Genset in fault |  | 22 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Genset to start |  | 21 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Gen available |  | 20 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Common shut down |  | 19 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Common electric trip |  | 18 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Common warning |  | 17 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Common notification |  | 16 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | No of starts | 4-5 Byte | 4-5 Byte | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | No of trips | 6-7 Byte | 6-7 Byte | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
20 | 65290 | Run Hours | Eng run hrs | 0-1 Byte | 2 Bytes | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Eng run min | 2-3 Byte | 2 Bytes | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Reserved | 4-7 Byte | 2 Bytes | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Reserved |  | 2 Bytes | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
21 | 65291 | Alarms registers 1 to 4 | Low oil pressure | 0-1 Byte | 12/15 bit
|  |  | High coolant temperature |  | 8/11 bit
|  |  | Low fuel level |  | 4/7 bit
|  |  | Water level switch |  | 0-3
|  |  | Under speed | 2-3 Byte | 28-31
|  |  | Over speed |  | 24-27
|  |  | to start |  | 20-23
|  |  | to stop |  | 16-19
|  |  | Generator low voltage | 4-5 Byte | 40-43
|  |  | Generator high voltage |  | 44-47
|  |  | Generator low frequency |  | 36-39
|  |  | Generator high frequency |  | 32-35
|  |  | Generator high current | 6-7 Byte | 60-63
|  |  | Generator overload |  | 56-59
|  |  | Unbalanced load |  | 52-55
|  |  | Emergency stop |  | 48-51
22 | 65292 | Alarm registers 5 to 8 | Fuel filter maintenance | 0-1 Byte | 4 to 7 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Oil filter maintenance |  | 08 to 11 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Charge alternator Failure |  | 12 to 15 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Air filter maintenance |  | 0-3 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Battery low voltage | 2-3 Byte | 28-31 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Battery high voltage |  | 24-27 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Temperature Circuit open |  | 20-23 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Reserved |  | 16-19 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Fuel theft | 4-5 Byte | 44-47 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | MPU lost |  | 40-43 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Oil pressure Open circuit |  | 36-39 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Reserved1 |  | 32-35 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Auxiliary input a | 6-7 Byte | 60-63
|  |  | Auxiliary input b |  | 56-59 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Auxiliary input c |  | 52-55 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Auxiliary input d |  | 48-51 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
23 | 65293 | Alarm registers 9 | Auxiliary input e | 0-1 Byte | Bit 12 - Bit 15 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Auxiliary input f |  | Bit 8 - Bit 11 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Auxiliary input g |  | Bit 4 - Bit 7 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Auxiliary input h |  | Bit 0 - Bit 3 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Unimplemented | 2-3 Byte | 28-31 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Unimplemented |  | 24-27 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Unimplemented |  | 20-23 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Unimplemented |  | 16-19 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Unimplemented | 4-5 Byte | 44-47 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Unimplemented |  | 40-43 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Unimplemented |  | 36-39 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Unimplemented |  | 32-35 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Unimplemented | 6-7 Byte | 60-63 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Unimplemented |  | 56-59 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Unimplemented |  | 52-55 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Unimplemented |  | 48-51 | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
24 | 65295 | Fuel level and Lube Oil pressure | Genset Rating | 6-7 Byte | 6-7 Byte | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Fuel in liters | 4-5 Byte | 4-5 Byte
|  |  | Reserved | 2-3 byte | 2-3 byte | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | LOP pressure | 0-1 Byte | 0-1 Byte
25 | 65296 | Genset Cumulative Kwh and KVAh | Generator Cumulative KWh | 0-3 Byte | 0-3 Byte | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Generator Cumulative KVAh | 4-7 Byte | 4-7 Byte | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
26 | 65297 | Genset Cumulative KVArh | Generator Cumulative KVArh | 0-3 Byte | 0-3 Byte | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28
|  |  | Reserved | 4-7 Byte | 4-7 Byte | Same as Exepected | Pass | Sahil Sheikh | 2024-03-28

## Timers
SEDEMAC |  | Test Report For : SW-GC2X-GC2115-RA6M2 |  |  |  |  | Doc # | SW-TEST_REPORT-GC2X-GC2115-RA6M2
[7 empty] | Rev #/ Rev Date | 0.27/21 June 2024
[7 empty] | Page # | 11 of 24
SR No. | Test Case ID | Description | Module/ Functionality Under Test | Corresponding SRS number | Expected Result | Actual Result | Results | Tested by | Date of testing
23 | GCU_23 | Set the crank time in from the GUI and start the DG | Crank Time | Functional 30 | GCU should give the cranking output for this time period. Start LED should glow for this time period when the start is pressed. | Working as expected | Pass | Purushottam P | 2023-03-04
|  | Set the crank rest time from the GUI. | Crank Rest Time | Functional 30 | After the first crank attempt, GCU should wait for this time period before giving next crank. Start LED should be off for this time period. | Working as expected | Pass | Purushottam P | 2023-03-04
|  | Set the safety monitoring delay from the GUI and create any shut down or warning alarm before timer expires. | Safety Monitoring Start Delay | Functional 30 | GCU should ignore all the alarms before safety monitoring delay timer is expired. After this timer expires, GCU should give the alarms. | Working as expected | Pass | Purushottam P | 2023-03-04
|  | Set the warm up delay for the GCU and start the Engine by keeping the auto load transfer enabled. | Warm Up Delay | Functional 55 | Start LED should keep blinking when the warm up delay is running. | Working as expected | Pass | Purushottam P | 2023-03-04
|  | This parameter should be checked in the AMF mode. In AMF mode turn the mains Off and ON for the several times after appropriate time of interval. | Mains Detect Delay | Functional 30 | DG should wait for this time period before turning OFF or ON if the change in the state of mains is detected. Mains should be healthy or unhealthy for this time period, then only the GCU will take action accordingly. | Working as expected | Pass | Purushottam P | 2023-03-04
|  | Set the alternator detect delay and generate any alternator related alarm. | Alternator Detect Delay | Functional 30 | GCU should detect all the alternator related alarms only after this delay timer is expired. Also the load should be transferred on the DG after this time delay is over | Working as expected | Pass | Purushottam P | 2023-03-04
|  | Set this timer in the GUI an give the start command. | Crank Start Delay | Functional 30 | GCU should give the crank attempts after this time period. Start LED should blink for this time period before the cranking starts. | Working as expected | Pass | Purushottam P | 2023-03-04
|  | Conduct this test in the AMF mode on the AMF panel. Set the Return to mains delay and start the DG by cutting Off the mains. | Return to mains delay | Functional 30 | When the mains is detected as healthy, then GCU should wait for the return to mains delay to give the stop command to the DG and switch the load on the mains. | Working as expected | Pass | Purushottam P | 2023-03-04
|  | Set the cooling down time. Start the DG and press the Stop button. | Engine Cooling Time | Functional 30 | When the stop command is received in the manual mode or in the auto mode, then GCU should open the DG contactor first and then it should stop the engine after cooling down time. | Working as expected | Pass | Purushottam P | 2023-03-04
|  | Start the engine. Issue the stop command and observe the stop solenoid output. | Stop action Delay | Functional 45, Functional 30 | Stop solenoid output should be high for the Stop action delay timer irrespective of the Engine status. GCU should give the to stop alarm if the DG does not stop for this time delay. | Working as expected | Pass | Purushottam P | 2023-03-04
|  | Set the additional stop delay and press the start key when this timer is going on. | Additional Stopping delay | Functional 30 | GCU should not give start command when we press start key during additional stop delay. | Working as expected | Pass | Purushottam P | 2023-03-04
|  | Commit ID: | Load Transfer | Functional 30 | DG should take this much amount of time to shift the load from mains to DG or vice versa | Working as expected | Pass | Purushottam P | 2023-03-04
|  | Set this time delay and observe the back light of the LCD when the GCU is idle. | Power Save mode | Functional 30 | LCD back light should get turned off after this time period. | Working as expected | Pass | Purushottam P | 2023-03-04
|  | Set the sounder alarm time, generate any audible alarm after DG On and observe the Sounder alarm output. | Sounder Alarm | Functional 36, Functional 41 | When any audible alarm occurs, then the sounder alarm output should be on for the time set in the sounder alarm timer. | Working as expected | Pass | Purushottam P | 2023-03-04
|  | Set the Test Mode time. Start the DG in test mode and check whether this mode auto expires after the set test mode time. | Test mode duration | Functional 30 | When DG is running in test mode, DG stops after the set test mode time. In Test mode while engien is OFF then START & AUTO LED keeps on blinking for test mode duration.In test mode when engine is ON Start Key is pressred then DG run for set duration & takes shutdown by taking timers as cooling ,stop action and addl stopping. | Working as expected | Pass | Purushottam P | 2023-03-04
|  | Set the screen change over time and observe the delay between the changing of two screens. | Screen Change Over Time | Functional 30 | GCU screen should change to the next screen after this time period. | Working as expected | Pass | Purushottam P | 2023-03-04

## Phase Sequence
SEDEMAC | Test Report For : SW-GC2X-GC2115-RA6M2 |  |  |  |  | Doc # | SW-TEST_REPORT-GC2X-GC2115-RA6M2
[6 empty] | Rev #/ Rev Date | 0.27/21 June 2024
[6 empty] | Page # | 12 of 24
DG and MAINS Phase Sequence
| Phase Sequence | Expected Result | For DG Actual Result | For Mains Actual Result | Pass/Fail | Tested By | Date of testing
| R-Y-B | No Alarm | No Alarm observed | No Alarm observed | Pass | Purushottam P | 2024-03-08
| B-R-Y | No Alarm | No Alarm observed | No Alarm observed | Pass | Purushottam P | 2024-03-08
| Y-B-R | No Alarm | No Alarm observed | No Alarm observed | Pass | Purushottam P | 2024-03-08
| R-B-Y | Alarm | Alarm observed | Alarm observed | Pass | Purushottam P | 2024-03-08
| Y-R-B | Alarm | Alarm observed | Alarm observed | Pass | Purushottam P | 2024-03-08
| B-Y-R | Alarm | Alarm observed | Alarm observed | Pass | Purushottam P | 2024-03-08

## SCP
SEDEMAC | Test Report For : SW-GC2X-GC2115-RA6M2 |  |  |  |  | Doc # | SW-TEST_REPORT-GC2X-GC2115-RA6M2
[6 empty] | Rev #/ Rev Date | 0.27/21 June 2024
[6 empty] | Page # | 13 of 24
For Automation test
| S1 - Shelter temprature sensor | [7 empty] | S2- Auxiliary sensor
|  | Expected Value |  | Actual Value | [5 empty] | Expected Value |  | Actual Value
| Resistance | Temperature | -2 V SCP | 0V SCP | +2 V SCP | RESULT |  |  | Resistance | Value | -2 V SCP | 0V SCP | +2 V SCP | RESULT
| 100 | 300 | 300 | 300 | 300 |  |  |  | 100 | 100 | 100 | 100 | 100
| 200 | 239 | 240 | 240 | 240 |  |  |  | 200 | 200 | 199.1 | 199 | 199.5
| 300 | 208 | 209 | 209 | 209 |  |  |  | 300 | 300 | 298.4 | 299 | 299.5
| 400 | 178 | 179 | 179 | 179 |  |  |  | 400 | 400 | 398.6 | 399.2 | 398.7
| 500 | 147 | 148 | 148 | 149 |  |  |  | 500 | 500 | 498.3 | 498.8 | 498.2
| 600 | 117 | 118 | 118 | 118 |  |  |  | 600 | 600 | 598.6 | 599.1 | 598.2
| 700 | 86 | 87 | 87 | 87 |  |  |  | 700 | 700 | 697.4 | 698.6 | 697.5
| 800 | 56 | 57 | 57 | 57 |  |  |  | 800 | 800 | 798.1 | 797.8 | 797.5
| 900 | 25 | 27 | 26 | 26 |  |  |  | 900 | 900 | 897.3 | 897.3 | 897.4
| 1000 | -5 | -4 | -4 | -4 |  |  |  | 1000 | 1000 | 996.8 | 996.7 | 997.1
|  | S3 sensor: 4-20mA LOP Sensor | [7 empty] | S3 sensor: 0-5V LOP Sensor
|  |  | Expected Value | Actual Value | [6 empty] | Expected Value |  | Actual Value (bar)
|  | mA | bar | bar | RESULT |  |  |  |  | Volt | bar | -2 V SCP | 0V SCP | +2 V SCP
|  | 4 | 0 | 0 | [5 empty] | 0.4 | 1 | 5.1 | 1.1 | 1
|  | 6 | 1 | 1 | [5 empty] | 0.9 | 2 | 6.1 | 2.1 | 1
|  | 7 | 2 | 2 | [5 empty] | 1.4 | 3 | 7 | 3 | 1
|  | 9 | 3 | 3.1 | [5 empty] | 1.9 | 4 | 8 | 4 | 1
|  | 10 | 4 | 4 | [5 empty] | 2.4 | 5 | 8.9 | 5.1 | 1
|  | 12 | 5 | 5 | [5 empty] | 2.9 | 6 | 9.9 | 5.9 | 1.9
|  | 14 | 6 | 6.1 | [5 empty] | 3.4 | 7 | 10 | 6.8 | 2.9
|  | 15 | 7 | 7 | [5 empty] | 3.9 | 8 | Overvalue | 7.8 | 3.8
|  | 17 | 8 | 8.1 | [5 empty] | 4.4 | 9 | Overvalue | 8.7 | 4.8
|  | 20 | 10 | 10 | [5 empty] | 4.9 | 10 | Overvalue | 9.7 | 5.7
S4 Sensor : Fuel 0-5 sensor tank with step
Actual Value (bar)
|  |  | Applied Voltage(Volts) | Expected | -2 V SCP | 0V SCP | +2 V SCP | RESULT
|  |  | 0.9 | 21.56 | NA | NA | NA
|  |  | 1.1 | 26.35 | NA | 27.9 | NA
|  |  | 1.6 | 38.33 | NA | NA | NA
|  |  | 2.4 | 57.5 | 89.3 | 57.3 | 9.4
|  |  | 2.9 | 67.98 | NA | NA | NA
|  |  | 3.4 | 75.6 | NA | NA | NA
|  |  | 3.9 | 83.22 | NA | 82.1 | NA
|  |  | 4.1 | 86.27 | NA | NA | NA
|  |  | 4.9 | 98.47 | NA | 96.6 | NA
|  |  | 4.9 | 98.47 | NA | 96.6 | NA

## Fuel sensor reference
SEDEMAC |  | Test Report For :SW-GC2X-GC2115-RA6M2 | [9 empty] | Doc # | SW-TEST_REPORT-GC2X-GC2115-RA6M2
[12 empty] | Rev #/ Rev Date | 0.27/21 June 2024
[12 empty] | Page # | 14 of 24
In automation scope
|  |  | Fuel sensor with tank |  |  |  | 0-5 V Fuel level calculation
| Step 1 |  |  | Voltage Range |  |  | Step 2 |  |  | Volume | Readings
| Tank dimensions |  |  | Sensor High Voltage (VDC) | Dynamic range | Sensor Low Voltage (VDC) | Tank dimensions |  |  | Fuel tank total Lit capacity capacity (Ltrs) | Sensor input voltage | Fuel Level in mm | H1 Height | H2 Height | Volume | % Lit | Observed % Lit | Observed Volume | Tested by | Date
| L1 (MM) | W (MM) | H1 (MM) |  |  |  | L2 (MM) | W (MM) | H2 (MM)
| 1000 | 600 | 200 | 5 | 4.5 | 0.5 | 0 | 0 | 0 | 120
[11 empty] | 5 | 200 | 200 | 0 | 120 | 100 | 100 | 120
[11 empty] | 4.8 | 191.1111 | 191.1111 | 0 | 114.6667 | 95.5556 | 95.9 | 115.1
[11 empty] | 4.5 | 177.7778 | 177.7778 | 0 | 106.6667 | 88.8889 | 89.2 | 107.1
| For Testing Tank with and without step: Set the 8 values in green and observe the readings as per Volume in % and Lit columns. Note: 1. Set W(Width) same at both places. 2. Set L2 = 0, H2 = 0 for tank without step. | [9 empty] | 4.3 | 168.8889 | 168.8889 | 0 | 101.3333 | 84.4444 | 85 | 102
[11 empty] | 4.1 | 160 | 160 | 0 | 96 | 80
[11 empty] | 3.9 | 151.1111 | 151.1111 | 0 | 90.6667 | 75.5556 | 75.9 | 91.1
[11 empty] | 3.7 | 142.2222 | 142.2222 | 0 | 85.3333 | 71.1111
[11 empty] | 3.5 | 133.3333 | 133.3333 | 0 | 80 | 66.6667
[11 empty] | 3.3 | 124.4444 | 124.4444 | 0 | 74.6667 | 62.2222 | 62.4 | 74.8
[11 empty] | 3.1 | 115.5556 | 115.5556 | 0 | 69.3333 | 57.7778
[11 empty] | 2.9 | 106.6667 | 106.6667 | 0 | 64 | 53.3333
[11 empty] | 2.8 | 102.2222 | 102.2222 | 0 | 61.3333 | 51.1111 | 51.2 | 61.4
[11 empty] | 2.7 | 97.7778 | 97.7778 | 0 | 58.6667 | 48.8889
[11 empty] | 2.6 | 93.3333 | 93.3333 | 0 | 56 | 46.6667
[11 empty] | 2.5 | 88.8889 | 88.8889 | 0 | 53.3333 | 44.4444 | 44.6 | 53.5
[11 empty] | 2.4 | 84.4444 | 84.4444 | 0 | 50.6667 | 42.2222
[11 empty] | 2.3 | 80 | 80 | 0 | 48 | 40
[11 empty] | 2.2 | 75.5556 | 75.5556 | 0 | 45.3333 | 37.7778 | 37.8 | 45.4
[11 empty] | 2.1 | 71.1111 | 71.1111 | 0 | 42.6667 | 35.5556
[11 empty] | 2 | 66.6667 | 66.6667 | 0 | 40 | 33.3333 | 33.2 | 39.8
[11 empty] | 1.9 | 62.2222 | 62.2222 | 0 | 37.3333 | 31.1111
[11 empty] | 1.8 | 57.7778 | 57.7778 | 0 | 34.6667 | 28.8889 | 29 | 34.7
[11 empty] | 1.7 | 53.3333 | 53.3333 | 0 | 32 | 26.6667
[11 empty] | 1.6 | 48.8889 | 48.8889 | 0 | 29.3333 | 24.4444
[11 empty] | 1.5 | 44.4444 | 44.4444 | 0 | 26.6667 | 22.2222
[11 empty] | 1.4 | 40 | 40 | 0 | 24 | 20 | 20 | 24
[11 empty] | 1.3 | 35.5556 | 35.5556 | 0 | 21.3333 | 17.7778
[11 empty] | 1.2 | 31.1111 | 31.1111 | 0 | 18.6667 | 15.5556
[11 empty] | 1.1 | 26.6667 | 26.6667 | 0 | 16 | 13.3333
[11 empty] | 1 | 22.2222 | 22.2222 | 0 | 13.3333 | 11.1111 | 11.1 | 13.4
[11 empty] | 0.9 | 17.7778 | 17.7778 | 0 | 10.6667 | 8.8889 | 8.7 | 10.5
[11 empty] | 0.8 | 13.3333 | 13.3333 | 0 | 8 | 6.6667 | 6.6 | 8
[11 empty] | 0.7 | 8.8889 | 8.8889 | 0 | 5.3333 | 4.4444 | 4.3 | 5.2
[11 empty] | 0.6 | 4.4444 | 4.4444 | 0 | 2.6667 | 2.2222 | 2.2 | 2.5
[11 empty] | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Tamper proofing test scenario
SEDEMAC |  | Test Report For : SW-GC2X-GC2115-RA6M2 | [5 empty] | Doc # | SW-TEST_REPORT-GC2X-GC2115-RA6M2
[8 empty] | Rev #/ Rev Date | 0.27/21 June 2024
[8 empty] | Page # | 15 of 24
NOT TESTED IN THIS BUILD | NOTE LOGIC | The test case for the invalid DG run is as below:
The voltage signals that GCU can detect is of greater than 20V RMS. If the above condition is valid and we see a ramp from 20Hz to 45Hz in less than 100ms then Invalid start otherwise it is Valid Start.
Sr # | Mode (Auto /Manual) | Condition | GCU state (Powered ON/OFF) ? | Engine started through | RAMP time | Alt wave feature enable (Yes/No) | Is "Invalid DG run" detected on GCU ? | Valid / Invalid DG run hour incremented ? | Expected observations | No. of start incremented ? | Detailed actual observations | Pass/Fail | Tested By | Date of testing
1 | Auto mode | Mains failed + BTS battery low + Shelter low | GCU ON | GCU | Ramp time is <100 m sec | NO | No | Valid DG run hour | NA | Yes | Not tested in this build
[6 empty] | YES | YES | Invalid DG run hour | invalid DG run hrs increment if ramp is given in short duration and alt wave deltection is enabled | No | Not tested in this build
3 | Manual mode with GCU key input | Any configuration | GCU ON | GCU | Ramp time >100 msec | Yes & No | No | Valid DG run hour | For both Alt wave feature enable (Yes/No) cases it should not give alarm | Yes | Not tested in this build
4 | Manual mode through with Panel push button | Any configuration | GCU ON | Panel | Ramp time >100 msec | Yes & No | No | Valid DG run hour | For both Alt wave feature enable (Yes/No) cases it should not give alarm | Yes | Not tested in this build
5 | Manual mode with direct crank of starter motor | Any configuration | GCU ON | Crank motor | Ramp time >100 msec | Yes & No | No | Valid DG run hour | For both Alt wave feature enable (Yes/No) cases it should not give alarm | Yes | Not tested in this build
7 | Manual mode through with Panel push button | Any configuration | GCU OFF when Engine started, later powered ON | Panel | Ramp time <100 msec | Yes | yes | Invalid DG run hour | invalid DG run hrs increment if ramp is given in short duration and alt wave deltection is enabled | No | Not tested in this build
[5 empty] | Ramp time >100 msec | No | No | Valid DG run hour | invalid DG run hrs should not increase if ramp is given more duration and alt wave deltection is disabled | Yes | Not tested in this build
9 | Manual mode with GCU key input & Panel push button or starter motor | Mains connector connected to genset voltage input connector when DG is OFF initially and then the DG started by accidental start. | GCU ON | GCU / Panel / Crank motor | Ramp time <100 msec | Yes | yes | Invalid DG run hour | invalid DG run hrs increment if ramp is given in short duration and alt wave deltection is enabled | No | Not tested in this build
[6 empty] | No | No | Valid DG run hour | invalid DG run hrs should not increase if ramp is given more duration and alt wave deltection is disabled | Yes | Not tested in this build
10 | Manual mode | Mains connector connected to genset voltage input connector when DG is OFF, LLOP switch alram is enable and keep state of LLOP switch at LOW.(LLOP switch assigned but crank not dosconnected using LLOP switch) | GCU ON | GCU / Panel / Crank motor | Ramp time < 100 msec | Yes | Yes | No | GCU will generate a stop command due to LLOP switch input and generate invalid DG run alarm | No | Not tested in this build
[6 empty] | No | No | No | GCU will generate a stop command due to LLOP switch input | Yes | Not tested in this build
10 | Manual mode | LLOP switch alram is enable and disconnect the crank using LLOP switch by making it high and connect the Mains connector to genset voltage input connector when DG is OFF.(LLOP switch assigned & crank dosconnected using LLOP switch) | GCU ON | GCU / Panel / Crank motor | Ramp time < 100 msec | Yes | Yes | Invalid DG run hour | GCU will keep the DG ON with DG invalid Run Alarm | Yes | Not tested in this build
[6 empty] | No | No | Valid DG run hour | GCU will keep the DG ON without DG invalid Run Alarm | Yes | Not tested in this build
11 | Manual mode with GCU key input / Panel push button / starter motor | Mains connector connected to genset voltage input connector after sucessful start of DG with normal working mode and after "Alt detect" delay time is lapsed | GCU ON | GCU / Panel / Crank motor | For 1st successful start ramp time is >100ms and after alternator detect delay ramp time < 100ms | Yes | No | None | The GCU will generate a stop command for low voltage / frequency And FAIL TO STOP alarm pop up | No | Not tested in this build
[6 empty] | No | No | None | The GCU will generate a stop command for low voltage / frequency AND FAIL TO STOP alarm pop up | No | Not tested in this build
12 | Manual mode with GCU key input / Panel push button / starter motor | Mains connector connected to genset voltage input connector after sucessful start of DG with normal working mode and before "Alt detect" delay time is lapsed | GCU ON | GCU / Panel / Crank motor | For 1st successful start ramp time is >100ms and before alternator detect delay Ramp time< 100ms | Yes | No | Valid DG run hour | NA | Yes | Not tested in this build
[6 empty] | No | No | Valid DG run hour | NA | Yes | Not tested in this build
13 | Manual mode with Panel push button / starter motor | Mains connector connected to genset voltage input connector when DG is OFF initially and then give start command to the DG and keep GCU power off | GCU OFF at start event and later powered ON | Panel / Crank motor | Ramp time <100 msec | Yes | Yes | Invalid DG run hour | There can be multiple combinations of the case |  | Not tested in this build
[6 empty] | No | No | Valid DG run hour | There can be multiple combinations of the case |  | Not tested in this build
14 | Auto / Manual mode with GCU key input / Panel push button / starter motor | DG started normally, after sometime there is a warning alarm and the alarm is cleared through panel reset push button | GCU ON and panel reset after DG start | GCU / Panel / Crank motor | Ramp time >100 msec | Yes | Yes | Valid DG run hour before reset and invalid DG run hour after reset | Valid DG run hour before reset and invalid DG run hour after reset.Initially no of Starts increments but does not increment after reset. | Yes but does Not increment after reset. | Not tested in this build
[6 empty] | No | No | Valid DG run hour | Valid DG run hour & no of Starts increment. | Yes | Not tested in this build
15 | Manual mode with GCU key input / Panel push button / starter motor As per default profile LLOP alarm enable | Connect Mains connector to genset voltage input connector after sucessful start of DG with normal working mode and before "Alt detect" delay time is lapsed. Stop DG by panel push button key. | GCU ON | GCU / Panel / Crank motor | For 1st successful start ramp time is >100ms and before alternator detect delay< 100ms | Yes | No | Valid DG run hour | OK (GCU should stops increasing engine run hours (valid) when DG is stopped using panel push button & gives LLOP & Fail to stop alarm | Yes | Not tested in this build
[6 empty] | No | No | Valid DG run hour | OK (GCU stops increasing engine run hours (valid) when DG is stopped using panel push button & gives LLOP & Fail to stop alarm) | Yes | Not tested in this build
16 | Manual mode with GCU key input / Panel push button / starter motor LLOP alarm disabled. | Connect Mains connector to genset voltage input connector after sucessful start of DG with normal working mode and before "Alt detect" delay time is lapsed. Stop DG by panel push button key. | GCU ON | GCU / Panel / Crank motor | For 1st successful start ramp time is >100ms and before alternator detect delay< 100ms | Yes | No | Valid DG run hour | OK (GCU stops increasing engine run hours (valid) when DG is stopped using panel push button will give Fail to stop alarm) | Yes | Not tested in this build
[6 empty] | No | No | Valid DG run hour | OK (GCU increases engine run hours (valid) when DG is stopped using panel push button) | Yes | Not tested in this build
Note: The expectation for the "Alt wave detect" logic to work properly, is to have the GCU ON while starting the genset
Note2: When GCU is ON: if the Engine starts by any means (GCU key or Panel button or direct cranking), GCU can sense that DG output voltage and frequency are rising gradually. GCU will treat this as "valid DG start", and so it will count "valid engine run-hours". By contrast, if someone connects mains into DG output connector: then GCU can sense that voltage and frequency rose very quickly, so GCU will treat this as "cheating" and so it will count "invalid engine run-hours". But suppose GCU is OFF and then someone starts the engine using panel button or direct cranking. This is not cheating. This is really engine running condition. After that he powers ON the GCU. Now GCU will not sense "gradual rise" of voltage and frequency. So GCU will think that this is cheating, and so it will count "invalid engine run-hours". This is not a bug in software. This is because of incorrect operation. Rule: never start the engine when GCU is OFF.

## Site battery run hours
SEDEMAC |  | Test Report For : SW-GC2X-GC2115-RA6M2 |  |  |  |  | Doc # | SW-TEST_REPORT-GC2X-GC2115-RA6M2
[7 empty] | Rev #/ Rev Date | 0.27/21 June 2024
[7 empty] | Page # | 16 of 24
| NOTE : | Following test cases to be considered with BTS HEALTHY/UNHEALTHY & contactor latched status YES/NO .While testing RUNNING status DG & MAINS Healthy status could be ignored unless other wise stated.
Expected results
Sr # | GCU Mode | Condition | Site battery run hour increment expected Yes/No | Actual Observations/ Remark | Pass/Fail | Tested by | Date of testing
1 | Auto | Keep DG in OFF state.Keep none of Genset and Mains contactor output latched (Make mains unhealthy) + apply BTS Voltage >40v (Set BTS healthy threshold is less than 40V) . | Yes | Run hours increases | Pass | Purushottam P | 2024-03-20
2 | Auto | Initially no Genset and Mains contactor latched. Simulate genset failed to start condition keeping the BTS and Mains unhealthy. .Keep BTS unhealthy means apply BTS >30v but less than set threshold. Here BTS healthy threshold is greather than 40v | Yes | Run hours increases | Pass | Purushottam P | 2024-03-20
3 | Manual | Feedback for Mains and Genset contactor are configured using DIgital Inputs and not latched (keep both inputs deactivated) + Apply BTS voltage > 40V | Yes | Run hours increases | Pass | Purushottam P | 2024-03-20
4 | Manual | First ensure that Feedback input for Mains and Genset contactor are not configured .Then apply healthy Mains or make DG running and latch any of contactor manually + apply BTS voltage > 40V | No | Run hours increases | Pass | Purushottam P | 2024-03-20
5 | Config Mode | Put GCU in Config mode and then observe Site Battery run hours screen on GCU .GCU should not increase Site Battery run hours . | No | Run hours does not increase | Pass | Purushottam P | 2024-03-20
6 | Auto or manual mode | Put GCU in Auto or manual mode & keep no contactor is latched and BTS voltage is < 40 is applied then Site Battery run hours should not increase. | Yes | Run hours increases | Pass | Purushottam P | 2024-03-20

## Password access master and user
SEDEMAC | Test Report For :SW-GC2X-GC2115-RA6M2 | [11 empty] | Doc # | SW-TEST_REPORT-GC2X-GC2115-RA6M2
[13 empty] | Rev #/ Rev Date | 0.27/21 June 2024
[13 empty] | Page # | 17 of 24
NOTE : FOR this GCU customer requested 'None parameter should be with editable access '.
| All parameters need to be tested considering the required changes. | [5 empty] | Actual result R1V20 |  |  | Actual result R1V22
| Menu | Submenu | Description | PIN 1(5555) | Pin 2 (0123) | Pin 3(9876) | Test result Pin 1 | Test result Pin 1 | Test result Pin 1 | Test result Pin 1 | Test result Pin 1 | Test result Pin 1 | Tested By | Date
| Module | General | Profile Name | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Power On Mode | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Power On Lamp Test | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Password Lock | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Display | Display Contrast (%) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Power Save Mode | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Modbus Communication | Comm Mode | Access | Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | MODBUS Slave ID | Access | Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | MODBUS Baudrate | Access | Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Parity Bit | Access | Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | MODBUS Map | Access | Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | BTS | Battery Montoring | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Low Battery Threshold | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Low Battery Monitoring Delay | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Genset Run Duration | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Cyclic Mode | Cyclic Mode | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Genset Off Time | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Genset On Time | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Night Restriction Mode | Night Mode | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Start Time | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Off Duration | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | AUTO MD SWITCH | AUTO MD SWITCH | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | MANUAL MODE TIME (Min) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | OUTPUT ON TIME (Min) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
| Digital Inputs | Digital Input A | Source | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | DIG Input A | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Polarity | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Action | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Activation | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Activation Delay (Sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Digital Input B | Source | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | DIG Input B | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Polarity | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Action | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Activation | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Activation Delay (Sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Digital Input C | Source | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | DIG Input C | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Polarity | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Action | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Activation | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Activation Delay (Sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Digital Input D | Source | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | DIG Input D | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Polarity | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Action | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Activation | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Activation Delay (Sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Digital Input E | Source | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | DIG Input E | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Polarity | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Action | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Activation | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Activation Delay (Sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Digital Input F | Source | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | DIG Input F | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Polarity | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Action | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Activation | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Activation Delay (Sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Digital Input G | Source | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | DIG Input G | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Polarity | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Action | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Activation | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Activation Delay (Sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Digital Input H | Source | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | DIG Input H | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Polarity | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Action | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Activation | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Activation Delay (Sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Digital Input I | Source | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | DIG Input I | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Polarity | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Action | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Activation | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Activation Delay (Sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
| Analog Inputs | LOP / DIG J | Sensor Selection | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Source | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | DIG Input J | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Polarity | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Action | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Activation | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Activation Delay(Sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | LOP Sensor Open Ckt Alarm | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R1 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | V1 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R2 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | V2 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R3 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | V3 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R4 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | V4 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R5 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | V5 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R6 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | V6 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R7 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | V7 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R8 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | V8 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R9 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | V9 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R10 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | V10 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Fuel Level / DIG K | Sensor selection | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Source | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | DIG Input K | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Polarity | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Action | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Activation | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Activation Delay (Sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Fuel Level Monitoring | Low Fuel Level Shutdown | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Low Fuel Level Shutdown threshold (%) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Low Fuel Level Notification | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Low Fuel Level Notification threshold (%) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Fuel Tank Capacity (Litre) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Fuel Theft Alarm | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Fuel Theft Threshold (%/Hr) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Fuel Consumption (Ltr/Hr) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Display Fuel In % | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R1 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | L1 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R2 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | L2 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R3 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | L3 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R4 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | L4 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R5 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | L5 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R6 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | L6 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R7 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | L7 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R8 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | L8 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R9 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | L9 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R10 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | L10 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R11 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | L11 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R12 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | L12 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R13 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | L13 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R14 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | L14 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R15 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | L15 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R16 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | L16 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R17 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | L17 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R18 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | L18 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R19 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | L19 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R20 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | L20 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Engine Temp / DIG L | Sensor selection | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Source | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | DIG Input L | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Polarity | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Action | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Activation | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Activation Delay (Sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Engine Temp Open Ckt Alarm | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R1 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | T1 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R2 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | T2 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R3 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | T3 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R4 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | T4 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R5 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | T5 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R6 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | T6 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R7 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | T7 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R8 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | T8 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R9 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | T9 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R10 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | T10 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Shelter Temp Sensor / Dig M | Sensor Selection | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Source | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | DIG Input M | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Polarity | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Action | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Activation | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Activation Delay(Sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Shelter Sensor Monitoring | High Temp Threshold | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Low Temp Threshold | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Monitoring Delay(Sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Genset Run Duration | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | S1 Sensor Open ckt alarm | Access | No Access | No Access | Fail | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-13
|  |  | R1 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Val1 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R2 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Val2 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R3 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Val3 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R4 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Val4 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R5 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Val5 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R6 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Val6 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R7 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Val7 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R8 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Val8 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R9 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Val9 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R10 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Val10 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | S2 SENSOR / Dig N | Sensor Selection | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Source | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | DIG Input N | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Polarity | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Action | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Activation | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Activation Delay(Sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | S2 SENSOR MONITORING | Action | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Threshold | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Threshold Type | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | S2 Sensor Open ckt alarm | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R1 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Val1 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R2 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Val2 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R3 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Val3 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R4 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Val4 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R5 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Val5 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R6 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Val6 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R7 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Val7 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R8 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Val8 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R9 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Val9 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | R10 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Val10 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | S3 SENSOR / Dig O | Sensor Selection | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Source | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | DIG Input O | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Polarity | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Action | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Activation | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Activation Delay(Sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | LOP Sensor Open Ckt Alarm | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | I1 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | V1 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | I2 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | V2 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | I3 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | V3 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | I4 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | V4 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | I5 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | V5 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | I6 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | V6 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | I7 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | V7 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | I8 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | V8 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | I9 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | V9 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | I10 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | V10 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | S4 SENSOR / Dig P | Sensor Selection | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Source | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | DIG Input P | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Polarity | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Action | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Activation | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Activation Delay(Sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Fuel Level Monitoring | Low Fuel Level Shutdown | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Low Fuel Level Shutdown threshold (%) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Low Fuel Level Notification | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Low Fuel Level Notification threshold (%) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Fuel Theft Alarm | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Fuel Theft Threshold (%/Hr) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Fuel Consumption (Ltr/Hr) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Display Fuel In Liters | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Sensor Low Voltage (Volt) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Sensor High Voltage (Volt) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Tank With Step | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Tank Width (mm) - For Both Steps | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Tank Step 1 Length (mm) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Tank Step 1 Heigth (mm) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Tank Step 2 Length (mm) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Tank Step 2 Heigth (mm) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
| Outputs | Digital Output A | Source | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Polarity | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Digital Output B | Source | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Polarity | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Digital Output C | Source | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Polarity | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Digital Output D | Source | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Polarity | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Digital Output E | Source | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Polarity | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Digital Output F | Source | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Polarity | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Digital Output G | Source | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Polarity | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Digital Output H | Source | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Polarity | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Digital Output I | Source | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Polarity | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Digital Output J | Source | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Polarity | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Digital Output K | Source | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Polarity | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Digital Output L | Source | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Polarity | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Digital Output M | Source | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Polarity | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Digital Output N | Source | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Polarity | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Digital Output O | Source | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Polarity | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Digital Output P | Source | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Polarity | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
| Timers | Cranking | Crank Hold Time (sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Crank Rest Time (sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Manual Start Delay (sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Auto Start Delay (sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | General | Safety Monotoring Delay (sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Mains Detect Delay (sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Alternator Detect Delay (sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Warm-up Delay (sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Return To Mains Delay (sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Engine Cooling Time (sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Stop Action Time (sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Additional Stopping Time (sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Load Transfer Delay (sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Power Save Mode Delay (sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Screen Changeover Time (sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Sounder Alarm Time (sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Test Mode Timer (min) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
| Generator | Alternator Config | Alternator Present | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Number of Poles | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | AC System | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Min Healthy Voltage (volt) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Min Healthy Frequency (Hz) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Phase Reversal Detection | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Phase Reversal Action | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Auto-load Transfer | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Alternator Wave Detection | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Voltage Monitoring | UV Shutdown Enable | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | UV Shutdown Threshold (volt) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | UV Warning Enable | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | UV Warning Threshold (volt) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | OV Shutdown Enable | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | OV Shutdown Threshold (volt) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | OV Warning Enable | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | OV Warning Threshold(volt) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Frequency Monitoring | UF Shutdown Enable | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | UF Shutdown Threshold (Hz) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | UF Warning Enable | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | UF Warning Threshold (Hz) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | OF Shutdown Enable | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | OF Shutdown Threshold (Hz) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | OF Warning Enable | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | OF Warning Threshold (Hz) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Current monitoring | CT Ratio | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Over-current Action | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Over-current Threshold (Amp) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Over-current Delay (sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | CT Correction Factor | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | CT Location | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Fan Current Monitoring | Monitoring Enable | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Fan CT Ratio | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Fan Current High Threshold | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Fan Current High Action | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Fan Current Low Threshold | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Fan Current Low Action | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Fan Current Delay (sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Load Monitoring | Generator Rating (kW) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Full Load Current (Amp/Phase) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Over-load Action | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Load Monitoring Threshold (%) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Over-load Delay (sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Unbalanced Load Action | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Unbalanced Load Threshold (%) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Unbalanced Load Delay (sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Unbalanced Load Activation Threshold (%) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
| Mains | Mains Config | Mains Monitoring | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Mains AC system | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Phase Reversal Detection | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Phase Reversal Action | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Three Phase calc for one phase | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Under-voltage Monitoring | Monitoring Enable | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Under-voltage Trip (Volt) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Under-voltage Return (Volt) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Over-voltage Monitoring | Monitoring Enable | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Over-voltage Trip (Volt) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Over-voltage Return (Volt) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Under-frequency Monitoring | Monitoring Enable | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Under-frequency Trip (Hz) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Under-frequency Return (Hz) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Over-frequency Monitoring | Monitoring Enable | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Over-frequency Trip (Hz) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Over-frequency Return (Hz) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
| Engine | Crank Disconnect | Start Attempts | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Disconnect On LOP Sensor | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Disconnect Pressure Threshold (bar) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Mon Pres Switch Before Start | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Mon Pres Sensor Before Start | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Disconnect On LLOP Switch | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | LLOP Switch Transient Time (sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Alternator Frequency (Hz) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Engine Speed (Speed) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Disconnect On Charging Alt Voltage | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Charging Alt Voltage Threshold | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Speed Monitoring | Engine Speed Sense Source | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Under-speed Shutdown | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Under-speed Threshold (RPM) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Under-speed Delay (sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Over-speed Threshold (RPM) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Over-speed Delay (sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Gross Over-speed Threshold (%) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Battery Monitoring | Monitoring Source | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Low Battery voltage action | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Low Battery Voltage Threshold (volt) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Low Battery Voltage Delay (sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | High Battery Voltage Action | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | High Battery Voltage Threshold (volt) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | High Battery Voltage Delay (sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Charging Alt Monitoring | Charging Alt Fail Action | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Chrg Alt Fail Threshold (volt) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Chrg Alt Fail Delay (sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Preheat | Preheat Timer (sec) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Engine Temperature Limit | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Engine Temperature Limit (degC) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Ambient Temp | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Engine Control Unit (ECU) | Engine Type | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Engine Speed | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Lube Oil Pressure | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Coolant Temperature | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Running Hours | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Battery Monitoring By J1939 | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Oil Temperature | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | ECU Communication Failure Action | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | ECU Communication Failure Activation | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | ECU Communication Failure Activation Delay | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | ECU Amber Lamp Action | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | ECU Amber Lamp Activation | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | ECU Amber Lamp Activation Delay | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | ECU Red Lamp Action | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | ECU Red Lamp Activation | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | ECU Red Lamp Activation Delay | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | ECU Malfunction Lamp Action | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | ECU Malfunction Lamp Activation | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | ECU Malfunction Lamp Activation Delay | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | ECU Protect Lamp Action | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | ECU Protect Lamp Activation | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | ECU Protect Lamp Activation Delay | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | GCU Source Address | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | ECU Source Address | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Lube Oil Pressure | Low Level Shutdown | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Shutdown Threshold (bar) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Low Level Warning | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Warning Threshold (bar) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Coolant Temperature | High Temp Shutdown | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Shutdown Threshold (deg C) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | High Temp Warning | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Warning Threshold (deg C) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Oil Temperature | High Temp Shutdown | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Shutdown Threshold (deg C) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | High Temp Warning | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Warning Threshold (deg C) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | Canopy Temperature | High Temp Shutdown | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Shutdown Threshold (deg C) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | High Temp Warning | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Warning Threshold (deg C) | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
| Maintenance | Filter | Alarm Action | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Due At Engine Hours | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Alarm Due Day | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Alarm Due Month | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Alarm Due Year | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Profile Name | Access | No Access | No Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  | EGR Timer | Timer Enable | No Access | No Access | Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Warning Time | No Access | No Access | Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Shutdown Time | No Access | No Access | Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04
|  |  | Heal Time | No Access | No Access | Access | Test Pass | Test Pass | Test Pass | Not Tested in this build | Not Tested in this build | Not Tested in this build | Rahul Hage | 2024-06-04

## Charging_Alternator_Graph
SEDEMAC | Test Report For : SW-TEST REPORT-EXECUTABLE-GC211X SP2-RA6M2 |  |  |  | Doc # | SW-TEST_REPORT-EXECUTABLE-GC211X- SP2-RA6M2
[5 empty] | Rev #/ Rev Date | 0.27/21 June 2024
[5 empty] | Page # | 18 of 24
Charging Alternator Power Consumption
| Tested on- SW-Executable-GC2X-GC2115 RA6M2 (FWR0V11) |  | Power consumption : 1.24 watt. | CA Power Consumption - 2.9 Watt | Tested By- Upendra K |  | Actual Result | Tested by | Date
| #VALUE! | [5 empty] | Charging Alternator Power Consumption=2.99W ,Pass | Upendra K | 2024-04-02
Commit ID:
RA6M2_R0_04
SW-TEST CASES -EXECUTABLE-GC211X-R5-RA6M2

## CT calibration factor readings
SEDEMAC | Test Report For :SW-GC2X-GC2116-RA6M2 |  |  |  |  | Doc # | SW-TEST_REPORT-GC2X-GC2116-RA6M2
[6 empty] | Rev #/ Rev Date | 0.27/21 June 2024
[6 empty] | Page # | 19 of 24
Value
| CT Ratio | 50 | 5 | 10
CT calibration factor readings
| Applied current (A) | set CT correction factor | Current on Fluke measured | Expected current on GCU | Actual Currrent on GCU (R,Y,B) | PASS/ FAIL | Tested by | Date of testing
| 1 | 0.9 | 1 | 9 | 8.9,8.9,9.0 | PASS | Upendra K | 2024-03-04
| 1 | 1 | 1 | 10 | 10.0,9.9,10.0 | PASS | Upendra K | 2024-03-04
| 1 | 1.1 | 1 | 11 | 10.9,10.9,10.9 | PASS | Upendra K | 2024-03-04
| 3.5 | 0.9 | 3.5 | 31.5 | 31.4,31.2,31.5 | PASS | Upendra K | 2024-03-04
| 3.5 | 1 | 3.5 | 35 | 34.9,34.8,35.0 | PASS | Upendra K | 2024-03-04
| 3.5 | 1.1 | 3.5 | 38.5 | 38.3,38.3,38.5 | PASS | Upendra K | 2024-03-04

## Battery Site Monitoring
SEDEMAC |  | Test Report For :SW-GC2X-GC2116-RA6M2 |  |  | Doc # | SW-TEST_REPORT-GC2X-GC2116-RA6M2
[5 empty] | Rev #/ Rev Date | 0.27/21 June 2024
[5 empty] | Page # | 20 of 24
| Set config |  |  | Expected result |  |  | Panel LED |  | Actual Results | Pass/Fail | Tested by (name of person) | Date of testing
| Site Battery | Shelter Temp | Mains Status | DG | Mains Contactor status | DG Contactor status | Mains LED | DG LED
| healthy | Healthy | Healthy | OFF | Latched | Unlatched | ON | OFF | As expected | Pass | Purushottam P | 2024-03-14
|  |  | Unhealthy | OFF | Unlatched | Unlatched | OFF | OFF | As expected | Pass | Purushottam P | 2024-03-14
| Healthy | Unhealthy | Healthy | OFF | Latched | Unlatched | ON | OFF | As expected | Pass | Purushottam P | 2024-03-14
|  |  | Unhealthy | ON | Unlatched | Latched | OFF | ON | As expected | Pass | Purushottam P | 2024-03-14
| Unhealthy | Healthy | Healthy | OFF | Latched | Unlatched | ON | OFF | As expected | Pass | Purushottam P | 2024-03-14
|  |  | Unhealthy | ON | Unlatched | Latched | OFF | ON | As expected | Pass | Purushottam P | 2024-03-14
| Unhealthy | Unhealthy | Healthy | OFF | Latched | Unlatched | ON | OFF | As expected | Pass | Purushottam P | 2024-03-14
|  |  | Unhealthy | ON | Unlatched | Latched | OFF | ON | As expected | Pass | Purushottam P | 2024-03-14
Phase recovery
| Set config |  |  | Expected result |  |  | Panel LED |  | Actual Results | Pass/Fail | Tested by (name of person) | Date of testing
| Site Battery | Shelter Temp | Mains Status | DG | Mains Contactor status | DG Contactor status | Mains LED | DG LED
| Unhealthy | Healthy
|  |  | Unhealthy | ON | Unlatched | Latched | OFF | ON | NOT tested in this build | NA | NA | NA
|  |  | Healthy | OFF | Latched | Unlatched | ON | OFF | NOT tested in this build | NA | NA | NA
| Healthy | Unhealthy | [6 empty] | NOT tested in this build | NA | NA | NA
|  |  | Unhealthy | ON | Unlatched | Latched | NA | NA | NOT tested in this build | NA | NA | NA
|  |  | Healthy | OFF | Latched | Unlatched | ON | OFF | NOT tested in this build | NA | NA | NA

## Contactor latching test cases
SEDEMAC |  | Test Report For :SW-GC2X-GC2116-RA6M2 |  |  |  |  | Doc # | SW-TEST_REPORT-GC2X-GC2116-RA6M2
[7 empty] | Rev #/ Rev Date | 0.27/21 June 2024
[7 empty] | Page # | 21 of 24
Test Cases
Sr.No | Conditions | Mode | Auto Load Transfer | Mains Contactor Action | DG contactor Action | Pass/Fail | Tested by | Date of testing
1 | Mains Healthy , Genset OFF | Manual | NA | Unlatch | Unlatch | Pass | Purushottam P | 2024-03-14
2 | Mains Healthy , Genset ON | Manual | Enable | Unlatch | Latch | Pass | Purushottam P | 2024-03-14
3 | Mains Unhealthy, Genset ON | Manual | Enable | Unlatch | Latch | Pass | Purushottam P | 2024-03-14
4 | Mains Unhealthy, Genset ON | Manual | Disable | Unlatch | Unlatch | Pass | Purushottam P | 2024-03-14
5 | Mains Unhealthy, Genset Fault | Manual | Disable | Unlatch | Unlatch | Pass | Purushottam P | 2024-03-14
6 | Mains Healthy , Genset ON | Manual | Disable | Unlatch | Unlatch | Pass | Purushottam P | 2024-03-14
7 | Mains Healthy , Genset OFF | Auto | NA | Latch | Unlatch | Pass | Purushottam P | 2024-03-14
8 | Mains Unhealthy, Genset ON | Auto | NA | Unlatch | Latch | Pass | Purushottam P | 2024-03-14
9 | Mains Unhealthy, Genset Fault | Auto | NA | Unlatch | Unlatch | Pass | Purushottam P | 2024-03-14
10 | Mains Healthy , Genset OFF | Auto ---> Manual | NA | Latch--->Unlach | Unlatch | Pass | Purushottam P | 2024-03-14
11 | Mains Unhealthy, Genset ON | Auto ---> Manual | Enable | Unlatch | Latch | Pass | Purushottam P | 2024-03-14
12 | Mains Unhealthy, Genset Fault | Auto ---> Manual | Enable | Unlatch | Unlatch | Pass | Purushottam P | 2024-03-14
13 | Mains Unhealthy, Genset ON | Auto ---> Manual | Disable | Unlatch | Latch--->Unlatch | Pass | Purushottam P | 2024-03-14
14 | Mains Healthy , Genset OFF | Manual ---> Auto | NA | Unlatch--->Latch | Unlatch | Pass | Purushottam P | 2024-03-14
15 | Mains Unhealthy, Genset ON | Manual ---> Auto | Enable | Unlatch | Latch | Pass | Purushottam P | 2024-03-14
16 | Mains Healthy, Genset ON | Manual ---> Auto | Disable | Unlatch---->Latch | Unlatch | Pass | Purushottam P | 2024-03-14
17 | Mains Healthy , Genset ON | Test | Disable | Unlatch | Unlatch | Pass | Purushottam P | 2024-03-14
18 | Mains Unhealthy, Genset ON | Test | Disable | Unlatch | Unlatch | Pass | Purushottam P | 2024-03-14
19 | Mains Healthy , Genset ON | Test | Enable | Unlatch | Unlatch | Pass | Purushottam P | 2024-03-14
20 | Mains Unhealthy, Genset ON | Test | Enable | Unlatch | Unlatch | Pass | Purushottam P | 2024-03-14
21 | Mains Healthy , Genset OFF | Auto Cyclic | NA | Latch | Unlatch | Pass | Purushottam P | 2024-03-14
22 | Mains Unhealthy, Genset ON | Auto Cyclic | NA | Unlatch | Latch | Pass | Purushottam P | 2024-03-14
23 | Mains Unhealthy, Genset Fault | Auto Cyclic | NA | Unlatch | Unlatch | Pass | Purushottam P | 2024-03-14
24 | Mains Unhealthy, Genset OFF during OFF time | Auto Cyclic | NA | Unlatch | Unlatch | Pass | Purushottam P | 2024-03-14

## DTC Faults
SEDEMAC |  | Test Report For :SW-GC2X-GC2115-RA6M2 |  |  |  |  | Doc # | SW-TESTREPORT-GC2X-GC2115-RA6M2
[7 empty] | Rev # Rev Date | 0.27/21 June 2024
[7 empty] | Page # | 22 of 24
ECU 162
| Sr No | SPN | FMI | PCODE | Description | Actual result R0V3 | Pass/Fail | Tested By | Date
| 1 | 97 | 5 | P2269 | Water in fuel detected | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 2 | 97 | 2 | P2169 | Error during sensor test-water in fuel | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 3 | 100 | 11 | P26DF | Low oil pressure | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 4 | 100 | 3 | P26E0 | Oil Press. Sensor Short to Battery | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 5 | 100 | 4 | P26E1 | Oil Press. Sensor Short to Ground | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 6 | 102 | 3 | P0108 | Boost pressure sensor voltage high | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 7 | 102 | 4 | P1111 | Boost pressure sensor voltage low | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 8 | 105 | 5 | P007D | Boost temperature sensor voltage high | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 9 | 105 | 6 | P007C | Boost temperature sensor voltage low | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 10 | 108 | 15 | P2227 | ECU internal Press. Sensor Above Normal | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 11 | 108 | 17 | P2230 | ECU internal Press. Sensor Below Normal | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 12 | 110 | 3 | P0118 | Coolant Temp Sesnor Votage High | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 13 | 110 | 4 | P0117 | Coolant Temp Sesnor Votage Low | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 14 | 157 | 13 | P018F | PRV Open Max Count Limit Reached | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 15 | 157 | 16 | P0095 | PRV forced to open by pressure increase | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 16 | 157 | 21 | P0096 | PRV forced to open by pressure shock | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 17 | 157 | 14 | P0194 | Rail pressure limiting valve opened | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 18 | 157 | 31 | P1110 | PRV reached max. allowed open time | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 19 | 157 | 3 | P0193 | Rail Press. Sensor Voltage above normal | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 20 | 157 | 4 | P0192 | Rail Press. Sensor Voltage Below normal | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 21 | 158 | 3 | P0561 | Battery Voltage Above Normal | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 22 | 158 | 4 | P0560 | Battery Voltage Below Normal | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 23 | 190 | 11 | P0219 | Engine overspeed detected | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 24 | 633 | 3 | P0087 | Rail Pressure Deviation Positive Side | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 25 | 633 | 4 | P0088 | Rail Pressure Deviation Negative Side | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 26 | 633 | 5 | P0089 | Maximum rail pressure limit exceeded | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 27 | 633 | 14 | P089C | maximum rail press. In limp home mode | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 28 | 636 | 8 | P0344 | Camshaft sensor signal error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 29 | 636 | 5 | P0340 | Camshaft sensor no signal error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 30 | 637 | 2 | P0336 | Crankshaft sensor signal error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 31 | 637 | 5 | P0335 | Crankshaft sensor no signal error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 32 | 651 | 5 | P0201 | Open load error - 1st Cylinder injector | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 33 | 651 | 3 | P1201 | Short circuit for cylinder1 injector | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 34 | 651 | 4 | P0262 | Shrt ckt from high to low side-cyl 1 | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 35 | 652 | 5 | P0205 | Open load error - 3rd Cylinder injector | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 36 | 652 | 3 | P1205 | Short circuit for cylinder 3 injector | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 37 | 652 | 4 | P0274 | Shrt ckt from high to low side-cyl 3 | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 38 | 653 | 5 | P0204 | Open load error - 4th Cylinder injector | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 39 | 653 | 3 | P1204 | Short circuit for cylinder 4 injector | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 40 | 653 | 4 | P0271 | Shrt ckt from high to low side-cyl 4 | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 41 | 654 | 5 | P0202 | Open load error - 2nd Cylinder injector | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 42 | 654 | 3 | P1202 | Short circuit for cylinder 2 injector | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 43 | 654 | 4 | P0265 | Shrt ckt from high to low side-cyl 2 | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 44 | 1136 | 3 | P0669 | ECU Temp. Above Normal | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 45 | 1136 | 4 | P0668 | ECU Temp Below Normal | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 46 | 1687 | 3 | P0697 | Voltage fault at sensor supply 3 | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 47 | 2432 | 3 | P0611 | DFC for status of drive limitation | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 48 | 2791 | 5 | P1403 | Open load error for EGR valve powerstage | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 49 | 2791 | 6 | P0408 | Over current error for EGR vlv H-bridge | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 50 | 2791 | 12 | P0488 | Over temp. error for EGR vlv H-bridge
| 51 | 2791 | 3 | P0490 | Motor pos. shrt ckt to battery for EGR | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 52 | 2791 | 4 | P1489 | Motor pos. shrt ckt to ground for EGR | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 53 | 2791 | 17 | P0409 | shrt ckt over load error for EGR vlv | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 54 | 2791 | 18 | P0488 | temp. dependent ovr current for EGR vlv
| 55 | 2791 | 14 | P0403 | Under vltg error for EGR vlv H-bridge | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 56 | 2791 | 7 | P042F | EGR valve Jammed at closed position | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 57 | 2791 | 31 | P042E | EGR valve Jammed at open position | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 58 | 2791 | 1 | P1406 | SRC high-sensor vltg for EGR vlv | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 59 | 2791 | 2 | P1405 | SRC low-sensor vltg for EGR vlv | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 60 | 2802 | 3 | P0563 | SRC high-battery voltage sensor | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 61 | 2802 | 4 | P0562 | SRC low-battery voltage sensor | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 62 | 3509 | 3 | P06B0 | Voltage fault at sensor supply 1 | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 63 | 3510 | 3 | P06B3 | Voltage fault at sensor supply 2 | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 64 | 5314 | 15 | P062B | injector booster voltage too low | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 65 | 5358 | 2 | P268C | Injector 1 IQA missing | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 66 | 5359 | 2 | P268D | Injector 3 IQA missing | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 67 | 5360 | 2 | P268E | Injector 4 IQA missing | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 68 | 5361 | 2 | P268F | Injector 2 IQA missing | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 69 | 5838 | 2 | P2BAC | EGR based inducement in first level | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 70 | 5838 | 3 | P2BA3 | EGR based inducement in final level | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 71 | 5838 | 15 | P26E2 | EGR based inducement in warning stage | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 72 | 5928 | 3 | P045D | Motor neg. shrt ckt to battery for EGR | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 73 | 5928 | 4 | P045C | Motor neg. shrt ckt to ground for EGR | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 74 | 7026 | 5 | P0251 | Fuel metering unit open load error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 75 | 7026 | 8 | P1620 | Over temp. of device of metering unit | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 76 | 7026 | 3 | P0252 | Shrt ckt to positive of metering unit | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 77 | 7026 | 4 | P0253 | Shrt ckt to ground of metering unit | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 78 | 8518 | 2 | P2146 | Injector bank - short circuit | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 79 | 516100 | 11 | P063B | Injection cut-off monitoring error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 80 | 516105 | 11 | P062C | Engine speed monitor error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 81 | 516106 | 11 | P1014 | Injector energizing time monitoring eror | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 82 | 516118 | 11 | P061B | Fault in energizing time comparison | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 83 | 516122 | 14 | P1639 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 84 | 516123 | 14 | P1642 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 85 | 516124 | 14 | P2641 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 86 | 516125 | 14 | P2643 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 87 | 516126 | 14 | P2645 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 88 | 516127 | 14 | P2646 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 89 | 516128 | 14 | P2647 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 90 | 516129 | 14 | P2648 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 91 | 516130 | 14 | P2640 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 92 | 516131 | 14 | P2654 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 93 | 516132 | 14 | P2650 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 94 | 516133 | 14 | P2651 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 95 | 516134 | 14 | P2652 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 96 | 516135 | 14 | P2649 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 97 | 516136 | 14 | P2655 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 98 | 516137 | 14 | P2656 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 99 | 516138 | 14 | P2657 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 100 | 516139 | 14 | P2658 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 101 | 516140 | 14 | P2659 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 102 | 516141 | 14 | P2660 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 103 | 516142 | 14 | P2661 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 104 | 516143 | 14 | P2662 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 105 | 516144 | 14 | P2663 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 106 | 516145 | 14 | P2654 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 107 | 516146 | 14 | P2664 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 108 | 516147 | 14 | P2665 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 109 | 516148 | 14 | P2666 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 110 | 516149 | 14 | P2667 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 111 | 516150 | 14 | P2674 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 112 | 516151 | 14 | P2668 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 113 | 516152 | 14 | P2669 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 114 | 516153 | 14 | P2670 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 115 | 516154 | 14 | P2672 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 116 | 516155 | 14 | P2673 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 117 | 516156 | 14 | P2679 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 118 | 516157 | 14 | P2675 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 119 | 516158 | 14 | P2676 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 120 | 516159 | 14 | P2677 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 121 | 516159 | 31 | P0606 | ECU internal error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 122 | 516160 | 14 | P2678 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 123 | 516160 | 31 | P0603 | ECU internal error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 124 | 516161 | 14 | P2680 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 125 | 516161 | 31 | P064C | ECU internal error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 126 | 516162 | 14 | P2681 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 127 | 516162 | 31 | P065C | ECU internal error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 128 | 516163 | 14 | P2682 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 129 | 516163 | 31 | P066C | ECU internal error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 130 | 516164 | 14 | P2671 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 131 | 516164 | 31 | P067C | ECU internal error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 132 | 516165 | 14 | P2684 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 133 | 516165 | 31 | P068C | ECU internal error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 134 | 516166 | 14 | P2685 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 135 | 516166 | 31 | P305D | ECU irregular switch OFF error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 136 | 516167 | 14 | P2686 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 137 | 516168 | 14 | P2683 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 138 | 516169 | 14 | P2690 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 139 | 516170 | 14 | P2687 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 140 | 516171 | 14 | P2688 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 141 | 516172 | 14 | P2689 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 142 | 516173 | 14 | P2691 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 143 | 516174 | 14 | P2692 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 144 | 516175 | 14 | P2693 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 145 | 516176 | 14 | P2694 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 146 | 516177 | 14 | P2699 | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 147 | 516178 | 31 | P160C | Error to report ABE active state | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 148 | 516179 | 11 | P161C | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 149 | 516180 | 31 | P162C | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 150 | 516181 | 3 | P063C | ECU internal Error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
| 151 | 516186 | 31 | P0682 | ECU main relay stuck error | Working as Expected | Pass | Sahil Sheikh | 2024-03-27
Duplicate string .
Duplicate string .
Duplicate string .
Duplicate string .
Duplicate string .
Duplicate string .
Duplicate string .
Duplicate string .
Duplicate string .
Duplicate string .
Fault code
P0659
P2671
P0658
P2670
P0563
P0562
P0560
P0560
P0115
P0115
P0118
P0117
P2B9C
PC113
PC113
PC11A
P206B
U0113
U0113
PC11A
P0563
P0562
P0611
P0219
P0070
P0070
P0070
P0340
P0340
P0335
P0335
P0425
P242A
P2265
P2269
P2205
P220E
P2205
P220F
P2200
P22FE
P2200
P229F
P2200
P22A1
P2200
P22A0
P2200
P229E
P2200
P229E
P2208
P2214
P2201
P229E
P2201
P229E
P2201
P220B
P0540
P0540
P0540
P0540
P062B
P21CF
P0202
P0203
P0204
P21D0
P0206
P062D
P062E
P21DC
P21DF
P0268
P0277
P0265
P0271
P0262
P0264
P0267
P0270
P0265
P0276
P0110
P00A3
P00A2
P0251
P0254
P0253
P0254
P0253
P0251
P060B
P061C
P1001
P0190
P061B
P068A
P05CB
P1003
P1006
P1005
P1007
P1008
P1009
P1010
P1011
P1004
P1013
P1014
P1015
P1016
P1012
P1018
P1019
P1020
P1021
P1022
P1023
P1024
P1025
P1026
P1017
P1027
P1028
P1029
P1030
P1031
P1032
P1033
P1034
P1036
P1037
P1038
P1039
P1040
P1041
P1042
P1043
P1044
P1045
P1035
P1047
P1048
P1049
P1046
P1050
P1051
P1052
P1053
P1054
P1055
P1056
P1057
P1058
P060C
P060C
P060C
P060C
P0524
P0523
P0522
P055F
P0198
P0198
P0197
P0108
P0107
P023D
P0089
P0089
P1037
P0089
P0087
P0088
P0088
P0088
P0191
P0191
P0193
P0192
P0603
P0603
P1702
P1703
P1704
P1706
P1706
P1707
P249E
P056D
P2C79
P24FE
P24FE
P20EE
P1561
P20A0
P3053
P3054
P20FE
P20FE
P20E9
P1567
P20F4
P3000
P2043
P208E
P2047
P20F5
P20F4
P202E
P202E
P05EB
P207F
P205A
P205A
U010E
P06F0
P06F0
P2062
P2062
P2062
P06F0
P06F0
P0475
P0475
P0641
P0651
P0615
P0615
P26E4
P26E4
P26E4
P26E4
P106B
P106C
P106D
P1074
P1075
P1076
P1077
P1078
P1079
P2530
P2100
P2100
P2100
P2101
P2103
P210D
P2102
P210C
P0638
P2101
P0638
P2112
P2115
P212D
P212C
P0428
P0427
P0438
P0437
P203F
P203F
P203F
P2047
P2049
P2048
P2047
P05EE
P05EE
P208A
P05EE
P05EE
P208A
P208A
P20A0
P20A0
P20A0
P20A0
P206A
P206A
P206A
P206A
P206A
P203A
P203A
P025A
P025A
P205A
P10FF
P0403
P0487
P213A
P0488
P2142
P213D
P2141
P213C
P213B
P0488
P213B
P0406
P0402
P0406
P0405
P0EC6
P0EC8
P0EC7
P0251
P268C
P268D
P268E
P268F
P106A
P1068
P1069
P1708
P1708
P1708
P1708
P1709
P0666
P0666
P204F
P05EE
P208A
P208A
P05EE
P05EE
P05EE
P05EE
P05EE
P05EE
P206A
P206A
P206A
P203A
P203A
P203A
P025A
P025A
P025A
P204F
P20FA
P20FB
P20FD
P20FC

## Checklist
SEDEMAC |  | Test Report For :SW-GC2X-GC2115-RA6M2 |  | Doc # | SW-TESTREPORT-GC2X-GC2115-RA6M2
|  |  |  | Rev #/ Rev Date | 0.27/21 June 2024
|  |  |  | Page # | 25 of 25
Test Report Review Checklist
Sr. No. | Item to be checked | Remark | Actual Remark
1 | H/w used is specified? | Yes/No | Yes
2 | Boot loader part number specified? | Yes/No | Yes
3 | Configuration files used are specified and attached? | Yes/No | CFGZ files has been flashed while flashing firmware package .
4 | Test rig information (part no. etc.) is specified? | Yes/No | Yes
5 | Source code information fully specified? | Yes/No | Yes
6 | Test cases performed: | All/Some | Some
7 | If "some": reason for not performing all test cases is specified? | Yes/No | Some other test cases perform in previous build
8 | Is the above reason approved by PL? | Yes/No | Yes
Questions below are only for those test cases that were actually performed:
9 | All test cases passed fully? | Yes/No | Yes
10 | Name of tester and date of testing specified for all test cases? | Yes/No | Yes
11 | If some test cases didn't pass fully: can the software be still released? | Yes/No | NA
12 | If "yes" above: is the justification specified? | Yes/No | NA
13 | Is the justification approved by PL? | Yes/No | NA
14 | Is the justification approved by concerned SYSE Lead Engineer? | Yes/No | NA
15 | Is the justification acceptable to this reviewer? | Yes/No | NA
16 | Any other comments? |  | No
Test Report Reviewed By: Aditya Joshi Date:24-Jun-2024 |  | Test Report Approved By: Mihir Bhalerao Date:24-Jun-2024

## TempSheet-Updates
SEDEMAC |  | Test Report For : SW-GC2X-GC2115-RA6M2 |  | Doc # | SW-TEST_GC2X-GC2115-RA6M2
|  |  |  | Rev #/ Rev Date | 0.27/21 June 2024
|  |  |  | Page # | 11 of 25
| Description |  | Current Sheet Status
FOR Reference
1 | GC211x controller should be developed for M&M for their CPCB4 gensets. The following modifications are required over and above the GC2115 R6.00 controller. | Implementation of J1939 protocol | added
2 |  | Addition of all CAN transmit list as per GC1114/5/6 controller here ECU162 CAN matrix, DTC codes etc. | added
3 |  | the engine types/screens/DTCs to be added to the CAN matrix in comments | Yet to be updated /TBD
4 | Padmini EGR ECU implementation |  | Yet to be updated /TBD
5 | DTC codes to be shared over MODBUS as per KG640C |  | Yet to be updated /TBD
6 | Fuel Rate from CAN should be shared over a new MODBUS register. |  | Yet to be updated /TBD
7 | Update unbalanced Load calculation |  | Yet to be updated /TBD
| GCU Site Data Update Tool v1.0 |  | seperate sheet added
| FOR Reference | Fuel relay ON timing
THrough Smart Config following parameters not getting updated correctyly in GC2115R1 firmware R0V07
Charge
ECU engine Type
GEn Singal to three phase selction
NOTE : Display of CAN parameters on MODBUS pending /TBD