## Sheet1
Sr. no | GEN Contactor output | GEN Feedback Input | GEN Feedback Status | Mains Contactor output | Mains Feedback Input | Mains Feedback Status | Load calculation | Actual | bGensetContactorOutputAssigned | bGensetContactorOutputIsPulseType | bGensetContactorOutputStatus | bGensetContactorFeedbackIsAssigned | bGensetContactorFeedbackInputStatus | bMainsContactorOutputAssigned | bMainsContactorOutputIsPulseType | bMainsContactorOutputStatus | bMainsContactorFeedbackIsAssigned | bMainsContactorFeedbackInputStatus | Expected output
1 | 1 | 1 | 1 | 0 | 1 | 1 | W | mains increases,but not considered | true | false | true | true | true | true | false | false | true | true | LOAD_ON_GEN
2 | 1 | 1 | 1 | 0 | 1 | 0 | G | ok,DG energy increases | true | false | true | true | true | true | false | false | true | false | LOAD_ON_GEN
3 | 1 | 1 | 1 | 0 | 0 | - | G | ok,DG energy increases | true | false | true | true | true | true | false | false | false | false | LOAD_ON_GEN
4 | 1 | 1 | 1 | Not Assigned | 1 | 1 | N | ok,mains energy increases | true | false | true | true | true | false | false | false | true | true | LOAD_NOT_ON_GEN_MAINS
5 | 1 | 1 | 1 | Not Assigned | 1 | 0 | W | NOT WORKING PROPERLY | true | false | true | true | true | false | false | false | true | false | LOAD_ON_GEN
6 | 1 | 1 | 1 | Not Assigned | 0 | - | G | ok,DG energy increases | true | false | true | true | true | false | false | false | false | false | LOAD_ON_GEN
7 | 1 | 1 | 0 | 0 | 1 | 1 | M | to check again ,High earth leak current ,DG stopped | true | false | true | true | false | true | false | false | true | true | LOAD_ON_MAINS
8 | 1 | 1 | 0 | 0 | 1 | 0 | N | ok,no load energy increases | true | false | true | true | false | true | false | false | true | false | LOAD_NOT_ON_GEN_MAINS
9 | 1 | 1 | 0 | 0 | 0 | - | N | ok | true | false | true | true | false | true | false | false | false | false | LOAD_NOT_ON_GEN_MAINS
10 | 1 | 1 | 0 | Not Assigned | 1 | 1 | M | NOT WORKING PROPERLY | true | false | true | true | false | false | false | false | true | true | LOAD_ON_MAINS
11 | 1 | 1 | 0 | Not Assigned | 1 | 0 | N | No Load Calculation | true | false | true | true | false | false | false | false | true | false | LOAD_NOT_ON_GEN_MAINS
12 | 1 | 1 | 0 | Not Assigned | 0 | - | N | No Load Calculation | true | false | true | true | false | false | false | false | false | false | LOAD_NOT_ON_GEN_MAINS
13 | 1 | 0 | - | 0 | 1 | 1 | M | ok | true | false | true | false | false | true | false | false | true | true | LOAD_ON_MAINS
14 | 1 | 0 | - | 0 | 1 | 0 | G | ok | true | false | true | false | false | true | false | false | true | false | LOAD_ON_GEN
15 | 1 | 0 | - | 0 | 0 | - | G | No Load Calculation | true | false | true | false | false | true | false | false | false | false | LOAD_ON_GEN
16 | 1 | 0 | - | Not Assigned | 1 | 1 | M | ok | true | false | true | false | false | false | false | false | true | true | LOAD_ON_MAINS
17 | 1 | 0 | - | Not Assigned | 1 | 0 | G | ok | true | false | true | false | false | false | false | false | true | false | LOAD_ON_GEN
18 | 1 | 0 | - | Not Assigned | 0 | - | G | ok | true | false | true | false | false | false | false | false | false | false | LOAD_ON_GEN
19 | 0 | 1 | 1 | 1 | 1 | 1 | W | Gives’ Fail to open gen contactor’ alarm & 0A load cuurent ,no DG & Mains Energy calculations | true | false | false | true | true | true | false | true | true | true | LOAD_ON_GEN
20 | 0 | 1 | 1 | 1 | 1 | 0 | G | ok | true | false | false | true | true | true | false | true | true | false | LOAD_ON_GEN
21 | 0 | 1 | 1 | 1 | 0 | - | G | ok | true | false | false | true | true | true | false | true | false | false | LOAD_ON_GEN
22 | 0 | 1 | 0 | 1 | 1 | 1 | M | NOT WORKING PROPERLY | true | false | false | true | false | true | false | true | true | true | LOAD_ON_MAINS
23 | 0 | 1 | 0 | 1 | 1 | 0 | N | ok | true | false | false | true | false | true | false | true | true | false | LOAD_NOT_ON_GEN_MAINS
24 | 0 | 1 | 0 | 1 | 0 | - | M | NOT WORKING PROPERLY | true | false | false | true | false | true | false | true | false | false | LOAD_ON_MAINS
25 | 0 | 0 | - | 1 | 1 | 1 | M | NOT WORKING PROPERLY | true | false | false | false | false | true | false | true | true | true | LOAD_ON_MAINS
26 | 0 | 0 | - | 1 | 1 | 0 | N | ok | true | false | false | false | false | true | false | true | true | false | LOAD_NOT_ON_GEN_MAINS
27 | 0 | 0 | - | 1 | 0 | - | M | NOT WORKING PROPERLY | true | false | false | false | false | true | false | true | false | false | LOAD_ON_MAINS
28 | 0 | 1 | 1 | 0 | 1 | 1 | N | 0A,no DG & no Mains Ennergy increases | true | false | false | true | true | true | false | false | true | true | LOAD_NOT_ON_GEN_MAINS
29 | 0 | 1 | 1 | 0 | 1 | 0 | W | NOT WORKING PROPERLY,in both cases DG ON & DG OFF | true | false | false | true | true | true | false | false | true | false | LOAD_ON_GEN
30 | 0 | 1 | 1 | 0 | 0 | - | G | NOT WORKING PROPERLYwith DG OFF,OK with DG running | true | false | false | true | true | true | false | false | false | false | LOAD_ON_GEN
31 | 0 | 1 | 1 | Not Assigned | 1 | 1 | N |  | true | false | false | true | true | false | false | false | true | true | LOAD_NOT_ON_GEN_MAINS
32 | 0 | 1 | 1 | Not Assigned | 1 | 0 | W |  | true | false | false | true | true | false | false | false | true | false | LOAD_ON_GEN
33 | 0 | 1 | 1 | Not Assigned | 0 | - | G |  | true | false | false | true | true | false | false | false | false | false | LOAD_ON_GEN
34 | 0 | 1 | 0 | 0 | 1 | 1 | M | ok,only mains Energy increasing | true | false | false | true | false | true | false | false | true | true | LOAD_ON_MAINS
35 | 0 | 1 | 0 | 0 | 1 | 0 | N | No load calculations observed,but LOAD current of 27 A gets displayed | true | false | false | true | false | true | false | false | true | false | LOAD_NOT_ON_GEN_MAINS
36 | 0 | 1 | 0 | 0 | 0 | - | N |  | true | false | false | true | false | true | false | false | false | false | LOAD_NOT_ON_GEN_MAINS
37 | 0 | 1 | 0 | Not Assigned | 1 | 1 | M |  | true | false | false | true | false | false | false | false | true | true | LOAD_ON_MAINS
38 | 0 | 1 | 0 | Not Assigned | 1 | 0 | N |  | true | false | false | true | false | false | false | false | true | false | LOAD_NOT_ON_GEN_MAINS
39 | 0 | 1 | 0 | Not Assigned | 0 | - | N |  | true | false | false | true | false | false | false | false | false | false | LOAD_NOT_ON_GEN_MAINS
40 | 0 | 0 | - | 0 | 1 | 1 | M |  | true | false | false | false | false | true | false | false | true | true | LOAD_ON_MAINS
41 | 0 | 0 | - | 0 | 1 | 0 | N |  | true | false | false | false | false | true | false | false | true | false | LOAD_NOT_ON_GEN_MAINS
42 | 0 | 0 | - | 0 | 0 | - | N |  | true | false | false | false | false | true | false | false | false | false | LOAD_NOT_ON_GEN_MAINS
43 | 0 | 0 | - | Not Assigned | 1 | 1 | M |  | true | false | false | false | false | false | false | false | true | true | LOAD_ON_MAINS
44 | 0 | 0 | - | Not Assigned | 1 | 0 | N |  | true | false | false | false | false | false | false | false | true | false | LOAD_NOT_ON_GEN_MAINS
45 | 0 | 0 | - | Not Assigned | 0 | - | N |  | true | false | false | false | false | false | false | false | false | false | LOAD_NOT_ON_GEN_MAINS
46 | Not Assigned | 1 | 1 | 1 | 1 | 1 | W |  | false | false | false | true | true | true | false | true | true | true | LOAD_ON_GEN
47 | Not Assigned | 1 | 1 | 1 | 1 | 0 | G |  | false | false | false | true | true | true | false | true | true | false | LOAD_ON_GEN
48 | Not Assigned | 1 | 1 | 1 | 0 | - | G |  | false | false | false | true | true | true | false | true | false | false | LOAD_ON_GEN
49 | Not Assigned | 1 | 0 | 1 | 1 | 1 | M |  | false | false | false | true | false | true | false | true | true | true | LOAD_ON_MAINS
50 | Not Assigned | 1 | 0 | 1 | 1 | 0 | N |  | false | false | false | true | false | true | false | true | true | false | LOAD_NOT_ON_GEN_MAINS
51 | Not Assigned | 1 | 0 | 1 | 0 | - | M |  | false | false | false | true | false | true | false | true | false | false | LOAD_ON_MAINS
52 | Not Assigned | 0 | - | 1 | 1 | 1 | M |  | false | false | false | false | false | true | false | true | true | true | LOAD_ON_MAINS
53 | Not Assigned | 0 | - | 1 | 1 | 0 | N |  | false | false | false | false | false | true | false | true | true | false | LOAD_NOT_ON_GEN_MAINS
54 | Not Assigned | 0 | - | 1 | 0 | - | M |  | false | false | false | false | false | true | false | true | false | false | LOAD_ON_MAINS
55 | Not Assigned | 1 | 1 | 0 | 1 | 1 | W |  | false | false | false | true | true | true | false | false | true | true | LOAD_ON_GEN
56 | Not Assigned | 1 | 1 | 0 | 1 | 0 | G |  | false | false | false | true | true | true | false | false | true | false | LOAD_ON_GEN
57 | Not Assigned | 1 | 1 | 0 | 0 | - | G |  | false | false | false | true | true | true | false | false | false | false | LOAD_ON_GEN
58 | Not Assigned | 1 | 1 | Not Assigned | 1 | 1 | W |  | false | false | false | true | true | false | false | false | true | true | LOAD_ON_GEN
59 | Not Assigned | 1 | 1 | Not Assigned | 1 | 0 | G |  | false | false | false | true | true | false | false | false | true | false | LOAD_ON_GEN
60 | Not Assigned | 1 | 1 | Not Assigned | 0 | - | G |  | false | false | false | true | true | false | false | false | false | false | LOAD_ON_GEN
61 | Not Assigned | 1 | 0 | 0 | 1 | 1 | M | NOT WORKING PROPERLY | false | false | false | true | false | true | false | false | true | true | LOAD_ON_MAINS
62 | Not Assigned | 1 | 0 | 0 | 1 | 0 | N | ok | false | false | false | true | false | true | false | false | true | false | LOAD_NOT_ON_GEN_MAINS
63 | Not Assigned | 1 | 0 | 0 | 0 | - | N | ok | false | false | false | true | false | true | false | false | false | false | LOAD_NOT_ON_GEN_MAINS
64 | Not Assigned | 1 | 0 | Not Assigned | 1 | 1 | M | NOT WORKING PROPERLY | false | false | false | true | false | false | false | false | true | true | LOAD_ON_MAINS
65 | Not Assigned | 1 | 0 | Not Assigned | 1 | 0 | N | ok | false | false | false | true | false | false | false | false | true | false | LOAD_NOT_ON_GEN_MAINS
66 | Not Assigned | 1 | 0 | Not Assigned | 0 | - | N | ok | false | false | false | true | false | false | false | false | false | false | LOAD_NOT_ON_GEN_MAINS
67 | Not Assigned | 0 | - | 0 | 1 | 1 | M | NOT WORKING PROPERLY | false | false | false | false | false | true | false | false | true | true | LOAD_ON_MAINS
68 | Not Assigned | 0 | - | 0 | 1 | 0 | N | ok | false | false | false | false | false | true | false | false | true | false | LOAD_NOT_ON_GEN_MAINS
69 | Not Assigned | 0 | - | 0 | 0 | - | N | ok | false | false | false | false | false | true | false | false | false | false | LOAD_NOT_ON_GEN_MAINS
70 | Not Assigned | 0 | - | Not Assigned | 1 | 1 | M | NOT WORKING PROPERLY | false | false | false | false | false | false | false | false | true | true | LOAD_ON_MAINS
71 | Not Assigned | 0 | - | Not Assigned | 1 | 0 | N | ok | false | false | false | false | false | false | false | false | true | false | LOAD_NOT_ON_GEN_MAINS
72 | Not Assigned | 0 | - | Not Assigned | 0 | - | G | With DG running & OFF ,no energy change is observed | false | false | false | false | false | false | false | false | false | false | LOAD_ON_GEN

## Sheet2
Sr. no | GEN Contactor output | GEN Feedback Input | GEN Feedback Status | Mains Contactor output | Mains Feedback Input | Mains Feedback Status | Load Calculation
1 | - | Assigned | Low | - | Assigned | Low | No Calculation
2 | - | Assigned | Low | - | Assigned | High | Mains
3 | - | Assigned | High | - | Assigned | Low | Genset
4 | - | Assigned | High | - | Assigned | High | Wrong
1 | OFF | Unassigned | - | - | Assigned | Low | No Calculation
2 | OFF | Unassigned | - | - | Assigned | High | Mains
3 | ON | Unassigned | - | - | Assigned | Low | Mains
4 | ON | Unassigned | - | - | Assigned | High | Wrong
1 | - | Assigned | Low | OFF | Unassigned | - | No Calculation
2 | - | Assigned | Low | ON | Unassigned | - | Genset
3 | - | Assigned | High | ON | Unassigned | - | Genset
4 | - | Assigned | High | ON | Unassigned | - | Wrong
1 | OFF | Unassigned | - | OFF | Unassigned | - | No Calculation
2 | OFF | Unassigned | - | ON | Unassigned | - | Mains
3 | ON | Unassigned | - | ON | Unassigned | - | Genset
4 | ON | Unassigned | - | ON | Unassigned | - | Wrong
1 | Unassigned | Unassigned | - | OFF | Unassigned | - | No Calculation
2 | Unassigned | Unassigned | - | ON | Unassigned | - | Mains
1 | Unassigned | Unassigned | - | - | Assigned | Low | No Calculation
2 | Unassigned | Unassigned | - | - | Assigned | High | Mains
1 | OFF | Unassigned | - | Unassigned | Unassigned | - | No Calculation
2 | ON | Unassigned | - | Unassigned | Unassigned | - | Genset
1 | - | Assigned | Low | Unassigned | Unassigned | - | No Calculation
2 | - | Assigned | High | Unassigned | Unassigned | - | Genset

## Sheet3
GCU stucks at preheating screen when started | volvo

## Sheet4
bGensetContactorOutputAssigned | bGensetContactorOutputIsPulseType | bGensetContactorOutputStatus | bGensetContactorFeedbackIsAssigned | bGensetContactorFeedbackInputStatus | bMainsContactorOutputAssigned | bMainsContactorOutputIsPulseType | bMainsContactorOutputStatus | bMainsContactorFeedbackIsAssigned | bMainsContactorFeedbackInputStatus | Expected output
true | false | true | true | true | true | false | false | true | true | LOAD_ON_GEN
true | false | true | true | true | true | false | false | true | false | LOAD_ON_GEN
true | false | true | true | true | true | false | false | false | false | LOAD_ON_GEN
true | false | true | true | true | false | false | false | true | true | LOAD_NOT_ON_GEN_MAINS
true | false | true | true | true | false | false | false | true | false | LOAD_ON_GEN
true | false | true | true | true | false | false | false | false | false | LOAD_ON_GEN
true | false | true | true | false | true | false | false | true | true | LOAD_ON_MAINS
true | false | true | true | false | true | false | false | true | false | LOAD_NOT_ON_GEN_MAINS
true | false | true | true | false | true | false | false | false | false | LOAD_NOT_ON_GEN_MAINS
true | false | true | true | false | false | false | false | true | true | LOAD_ON_MAINS
true | false | true | true | false | false | false | false | true | false | LOAD_NOT_ON_GEN_MAINS
true | false | true | true | false | false | false | false | false | false | LOAD_NOT_ON_GEN_MAINS
true | false | true | false | false | true | false | false | true | true | LOAD_ON_MAINS
true | false | true | false | false | true | false | false | true | false | LOAD_ON_GEN
true | false | true | false | false | true | false | false | false | false | LOAD_ON_GEN
true | false | true | false | false | false | false | false | true | true | LOAD_ON_MAINS
true | false | true | false | false | false | false | false | true | false | LOAD_ON_GEN
true | false | true | false | false | false | false | false | false | false | LOAD_ON_GEN
true | false | false | true | true | true | false | true | true | true | LOAD_ON_GEN
true | false | false | true | true | true | false | true | true | false | LOAD_ON_GEN
true | false | false | true | true | true | false | true | false | false | LOAD_ON_GEN
true | false | false | true | false | true | false | true | true | true | LOAD_ON_MAINS
true | false | false | true | false | true | false | true | true | false | LOAD_NOT_ON_GEN_MAINS
true | false | false | true | false | true | false | true | false | false | LOAD_ON_MAINS
true | false | false | false | false | true | false | true | true | true | LOAD_ON_MAINS
true | false | false | false | false | true | false | true | true | false | LOAD_NOT_ON_GEN_MAINS
true | false | false | false | false | true | false | true | false | false | LOAD_ON_MAINS
true | false | false | true | true | true | false | false | true | true | LOAD_NOT_ON_GEN_MAINS
true | false | false | true | true | true | false | false | true | false | LOAD_ON_GEN
true | false | false | true | true | true | false | false | false | false | LOAD_ON_GEN
true | false | false | true | true | false | false | false | true | true | LOAD_NOT_ON_GEN_MAINS
true | false | false | true | true | false | false | false | true | false | LOAD_ON_GEN
true | false | false | true | true | false | false | false | false | false | LOAD_ON_GEN
true | false | false | true | false | true | false | false | true | true | LOAD_ON_MAINS
true | false | false | true | false | true | false | false | true | false | LOAD_NOT_ON_GEN_MAINS
true | false | false | true | false | true | false | false | false | false | LOAD_NOT_ON_GEN_MAINS
true | false | false | true | false | false | false | false | true | true | LOAD_ON_MAINS
true | false | false | true | false | false | false | false | true | false | LOAD_NOT_ON_GEN_MAINS
true | false | false | true | false | false | false | false | false | false | LOAD_NOT_ON_GEN_MAINS
true | false | false | false | false | true | false | false | true | true | LOAD_ON_MAINS
true | false | false | false | false | true | false | false | true | false | LOAD_NOT_ON_GEN_MAINS
true | false | false | false | false | true | false | false | false | false | LOAD_NOT_ON_GEN_MAINS
true | false | false | false | false | false | false | false | true | true | LOAD_ON_MAINS
true | false | false | false | false | false | false | false | true | false | LOAD_NOT_ON_GEN_MAINS
true | false | false | false | false | false | false | false | false | false | LOAD_NOT_ON_GEN_MAINS
false | false | false | true | true | true | false | true | true | true | LOAD_ON_GEN
false | false | false | true | true | true | false | true | true | false | LOAD_ON_GEN
false | false | false | true | true | true | false | true | false | false | LOAD_ON_GEN
false | false | false | true | false | true | false | true | true | true | LOAD_ON_MAINS
false | false | false | true | false | true | false | true | true | false | LOAD_NOT_ON_GEN_MAINS
false | false | false | true | false | true | false | true | false | false | LOAD_ON_MAINS
false | false | false | false | false | true | false | true | true | true | LOAD_ON_MAINS
false | false | false | false | false | true | false | true | true | false | LOAD_NOT_ON_GEN_MAINS
false | false | false | false | false | true | false | true | false | false | LOAD_ON_MAINS
false | false | false | true | true | true | false | false | true | true | LOAD_ON_GEN
false | false | false | true | true | true | false | false | true | false | LOAD_ON_GEN
false | false | false | true | true | true | false | false | false | false | LOAD_ON_GEN
false | false | false | true | true | false | false | false | true | true | LOAD_ON_GEN
false | false | false | true | true | false | false | false | true | false | LOAD_ON_GEN
false | false | false | true | true | false | false | false | false | false | LOAD_ON_GEN
false | false | false | true | false | true | false | false | true | true | LOAD_ON_MAINS
false | false | false | true | false | true | false | false | true | false | LOAD_NOT_ON_GEN_MAINS
false | false | false | true | false | true | false | false | false | false | LOAD_NOT_ON_GEN_MAINS
false | false | false | true | false | false | false | false | true | true | LOAD_ON_MAINS
false | false | false | true | false | false | false | false | true | false | LOAD_NOT_ON_GEN_MAINS
false | false | false | true | false | false | false | false | false | false | LOAD_NOT_ON_GEN_MAINS
false | false | false | false | false | true | false | false | true | true | LOAD_ON_MAINS
false | false | false | false | false | true | false | false | true | false | LOAD_NOT_ON_GEN_MAINS
false | false | false | false | false | true | false | false | false | false | LOAD_NOT_ON_GEN_MAINS
false | false | false | false | false | false | false | false | true | true | LOAD_ON_MAINS
false | false | false | false | false | false | false | false | true | false | LOAD_NOT_ON_GEN_MAINS
false | false | false | false | false | false | false | false | false | false | LOAD_ON_GEN