## MODBUS
SEDEMAC |  | List of MODBUS Registers | Doc # | SW-MODBUS Registers-GC1x-KG640
|  |  | Rev # / Rev Date | R0.00 / 1-Oct-2021
|  | SW-GC1x-KG640 12028 | Page # | 1 of 1
MODBUS Input register map for KG640
| Reg Offset | Value | Scale Factor | Measuring Unit | Bits/Sign
| 0 | Protocol version | 1 |  | Unsigned
| 1 | Reserved | NA | NA | NA
| 2 | Lub. Oil pressure | 0.1 | Bar/Deg C | Unsigned
| 3 | Coolant temperature | 0.1 | Deg C | Unsigned
| 4 | Fuel level | 1 | % | Unsigned
| 5 | Charge alternator voltage | 1 | V | Unsigned
| 6 | Battery voltage | 0.1 | V | Unsigned
| 7 | No of Starts | 1 | - | Unsigned
| 8 | No of Trips | 1 | - | Unsigned
| 9 | Engine run time (Hours) | 1 | Hours | Unsigned
| 10 | Engine run time (Minutes) | 1 | Minutes | Unsigned
| 11 | Engine speed | 1 | RPM | Unsigned
| 12 | Generator R frequency | 0.1 | Hz | Unsigned
| 13 | Generator Y frequency | 0.1 | Hz | Unsigned
| 14 | Generator B frequency | 0.1 | Hz | Unsigned
| 15 | Generator L1-N voltage | 0.1 | V | Unsigned
| 16 | Generator L2-N voltage | 0.1 | V | Unsigned
| 17 | Generator L3-N voltage | 0.1 | V | Unsigned
| 18 | Generator L1-L2 voltage | 0.1 | V | Unsigned
| 19 | Generator L2-L3 voltage | 0.1 | V | Unsigned
| 20 | Generator L3- L1 voltage | 0.1 | V | Unsigned
| 21 | Generator L1 current | 0.1 | A | Unsigned
| 22 | Generator L2 current | 0.1 | A | Unsigned
| 23 | Generator L3 current | 0.1 | A | Unsigned
| 24 | Generator L1 power | 0.1 | KW | Unsigned
| 25 | Generator L2 power | 0.1 | KW | Unsigned
| 26 | Generator L3 power | 0.1 | KW | Unsigned
| 27 | Generator total power | 0.1 | KW | Unsigned
| 28 | Generator L1 apparent power | 0.1 | KVA | Unsigned
| 29 | Generator L2 apparent power | 0.1 | KVA | Unsigned
| 30 | Generator L3 apparent power | 0.1 | KVA | Unsigned
| 31 | Generator total apparent power | 0.1 | KVA | Unsigned
| 32 | Generator L1 reactive power | 0.1 | KVAr | Unsigned
| 33 | Generator L2 reactive power | 0.1 | KVAr | Unsigned
| 34 | Generator L3 reactive power | 0.1 | KVAr | Unsigned
| 35 | Generator total reactive power | 0.1 | KVAr | Unsigned
| 36 | Generator power factor L1 | 0.01 |  | Unsigned
| 37 | Generator power factor L2 | 0.01 |  | Unsigned
| 38 – 39 | Generator power factor L3 | 0.01 |  | Unsigned
| 40 – 41 | Generator average power factor | 0.01 |  | Unsigned
| 42 – 43 | Generator cumulative energy | 0.1 | KWH | Unsigned
| 44 | Generator cumulative apparent energy | 0.1 | KVA | Unsigned
| 45 | Generator Cumulative reactive energy | 0.1 | KVAr | Unsigned
| 46 | Mains L1-N voltage | 0.1 | V | Unsigned
| 47 | Mains L2-N voltage | 0.1 | V | Unsigned
| 48 | Mains L3-N voltage | 0.1 | V | Unsigned
| 49 | Mains L1-L2 voltage | 0.1 | V | Unsigned
| 50 | Mains L2-L3 voltage | 0.1 | V | Unsigned
| 51 | Mains L3-L1 voltage | 0.1 | V | Unsigned
| 52 | Mains R frequency | 0.1 | Hz | Unsigned
| 53 | Mains Y frequency | 0.1 | Hz | Unsigned
| 54 | Mains B frequency | 0.1 | Hz | Unsigned
| 55 | Alarm 1
|  | Low oil pressure |  |  | 13/16-16/16
|  | High coolant temperature |  |  | 9/16-12/16
|  | Low fuel level |  |  | 5/16-8/16
|  | Low water level Switch |  |  | 1/16-4/16
| 56 | Alarm 2
|  | Under speed |  |  | 13/16-16/16
|  | Over speed |  |  | 9/16-12/16
|  | Fail to start |  |  | 5/16-8/16
|  | Fail to stop |  |  | 1/16-4/16
| 57 | Alarm 3
|  | Reserved |  |  | 13/16-16/16
|  | Reserved |  |  | 9/16-12/16
|  | Generator low frequency |  |  | 5/16-8/16
|  | Generator high frequency |  |  | 1/16-4/16
| 58 | Alarm 4
|  | Generator high current |  |  | 13/16-16/16
|  | Generator overload |  |  | 9/16-12/16
|  | Unbalanced load |  |  | 5/16-8/16
|  | Emergency stop |  |  | 1/16-4/16
| 59 | Alarm 5
|  | Charge alternator failure |  |  | 13/16-16/16
|  | Maintenance alarm |  |  | 9/16-12/16
| 60 | Alarm 6
|  | Battery low voltage |  |  | 13/16-16/16
|  | Battery high voltage |  |  | 9/16-12/16
|  | Reserved |  |  | 5/16-8/16
|  | Engine temperature circuit open |  |  | 1/16-4/16
| 61 | Alarm 7
|  | Fuel theft |  |  | 13/16-16/16
|  | Reserved |  |  | 9/16-12/16
|  | Analogue sensor 2 circuit open |  |  | 5/16-8/16
|  | Reserved |  |  | 1/16-4/16
| 62 | Alarm 8
|  | Auxiliary Input A |  |  | 13/16-16/16
|  | Auxiliary Input B |  |  | 9/16-12/16
|  | Auxiliary Input C |  |  | 5/16-8/16
|  | Auxiliary Input D |  |  | 1/16-4/16
| 63 | Alarm 9
|  | Auxiliary Input E |  |  | 13/16-16/16
|  | Auxiliary Input F |  |  | 9/16-12/16
|  | Auxiliary Input G |  |  | 5/16-8/16
|  | Auxiliary Input H |  |  | 1/16-4/16
| 64 | Alarm 10
|  | Gen R phase low volt |  |  | 13/16-16/16
|  | Gen R phase high volt |  |  | 9/16-12/16
|  | Gen Y phase low volt |  |  | 5/16-8/16
|  | Gen Y phase high volt |  |  | 1/16-4/16
| 65 | Alarm 11
|  | Gen B phase low volt |  |  | 13/16-16/16
|  | Gen B phase high volt |  |  | 9/16-12/16
|  | DG phase rotation |  |  | 5/16-8/16
|  | Mains phase rotation |  |  | 1/16-4/16
| 66 | Alarm 12
|  | High canopy temperature |  |  | 13/16-16/16
|  | V belt broken |  |  | 9/16-12/16
|  | Reserved |  |  | 5/16-8/16
|  | Reserved |  |  | 1/16-4/16
| 67 | Alarm 13
|  | Reserved |  |  | 13/16-16/16
|  | Reserved |  |  | 9/16-12/16
|  | Reserved |  |  | 5/16-8/16
|  | Reserved |  |  | 1/16-4/16
| 68 | Alarm 14
|  | Reserved |  |  | 13/16-16/16
|  | Reserved |  |  | 9/16-12/16
|  | Reserved |  |  | 5/16-8/16
|  | Reserved |  |  | 1/16-4/16
| 69 | Alarm 15
|  | Reserved |  |  | 13/16-16/16
|  | Reserved |  |  | 9/16-12/16
|  | Reserved |  |  | 5/16-8/16
|  | Reserved |  |  | 1/16-4/16
| 70 | Alarm 16
|  | Reserved |  |  | 13/16-16/16
|  | Reserved |  |  | 9/16-12/16
|  | Alternator Vtg Lost |  |  | 5/16-8/16
|  | Speed detected |  |  | 1/16-4/16
| 71 | Reserved
|  | Reserved |  |  | 16/16
|  | Reserved |  |  | 15/16
|  | Reserved |  |  | 14/16
|  | Reserved |  |  | 13/16
|  | Reserved |  |  | 2016-12-01
|  | Reserved |  |  | 2016-11-01
|  | Reserved |  |  | 2016-10-01
|  | Reserved |  |  | 2016-09-01
|  | Reserved |  |  | 2016-08-01
|  | Reserved |  |  | 2016-07-01
|  | Reserved |  |  | 2016-06-01
|  | Reserved |  |  | 2016-05-01
|  | Reserved |  |  | 2016-04-01
|  | Reserved |  |  | 2016-03-01
|  | Reserved |  |  | 2016-02-01
|  | Reserved |  |  | 2016-01-01
| 72 | Input Output Diagnostics
|  | Digital Input A |  |  | 16/16
|  | Digital Input B |  |  | 15/16
|  | Digital Input C |  |  | 14/16
|  | Digital Input D |  |  | 13/16
|  | Digital Input E |  |  | 2016-12-01
|  | Digital Input F |  |  | 2016-11-01
|  | Digital Input G |  |  | 2016-10-01
|  | Digital Input H |  |  | 2016-09-01
|  | Digital Output A |  |  | 2016-08-01
|  | Digital Output B |  |  | 2016-07-01
|  | Digital Output C |  |  | 2016-06-01
|  | Digital Output D |  |  | 2016-05-01
|  | Digital Output E |  |  | 2016-04-01
|  | Digital Output F |  |  | 2016-03-01
|  | Unimplemented |  |  | 2016-02-01
|  | Unimplemented |  |  | 2016-01-01
| 73 | DG Status
|  | Load on DG | TRUE (1), FALSE (0) |  | 16/16
|  | Current DG Status | Running (1), Stopped (0) |  | 15/16
|  | DG Stopped normally | TRUE (1), FALSE (0) |  | 14/16
|  | DG Stopped with fault | TRUE (1), FALSE (0) |  | 13/16
|  | DG Mode | Auto (1), Manual(0) |  | 2016-12-01
|  | Common shutdown | TRUE (1), FALSE (0) |  | 2016-11-01
|  | Common electrical trip | TRUE (1), FALSE (0) |  | 2016-10-01
|  | Common warning | TRUE (1), FALSE (0) |  | 2016-09-01
|  | Common Notification | TRUE (1), FALSE (0) |  | 2016-08-01
|  | Load On Mains | TRUE (1), FALSE (0) |  | 2016-07-01
|  | Unimplemented | TRUE (1), FALSE (0) |  | 6/16-1/16
| 74 | Command Status |  |  | Unsigned
|  | Write command | DG Started (1)
|  | Write command | DG Stopped (2)
|  | Read command | DG already On (3)
|  | Read command | DG already Off (4)
|  | Read command | DG in manual mode (5)
|  | Read command | DG Not started (6)
| 75 | Alarm 17
|  | High Oil Pressure detected WARNING |  |  | 13/16-16/16
|  | Speed Fault |  |  | 9/16-12/16
|  | Reserved |  |  | 5/16-8/16
|  | Reserved |  |  | 1/16-4/16
MODBUS Holding Register Map For GCU
| Reg Offset | Value | Note | Bits/ Sign
| 0 | Command Register | Send (0x01) to Start DG
Send (0x02) to Stop DG
Command Status is updated in Status register
| 1 | Operating Mode | Send (0x01) to toggle Current Mode | Unsigned
Auto Mode is to operate DG remotely
Manual is to operate DG with Key press