SRS For KG640 (SW-GC1X-KG640X)

SRS Revision History:

| SRS Rev No | Date | Changes Made |
| --- | --- | --- |
| 5.00 | 1 Oct 2021 | - Add the parameter charging alternator voltage monitoring through battery. |
| 4.01 | 3 Mar 2021 | - LOT and Temperature sensor range change - Open ckt action change for LOT, Fuel and 4-20mA sensors. |
| 4.00 | 19 Nov 2020 | - Add New product in this series KG640I - Add LOT sensor in the list of Fuel sensor - Add Output Fuel Solenoid - Add Input Remote Start Stop in manual mode - Remove Auto mode functionality - Keep separate button for alarm ACK |
| 3.00 | 23 May 2020 | - Make the firmware compatible with Smart Flash, port it to new bootloader: GC1X-B04-R0V1 - Make the firmware compatible to new hardware PCB board derived from PCB SM0010254. - New 4-20mA input is to be added for LOP measurement as channel S2. |
| 2.00 | 9 May 2019 | Semi-Auto Mode digital input added. |
| 1.00 | 29 Jun 2018 | Engine Serial number should support 25 alphanumeric characters. MODBUS map should be compatible with KG645 R3. It should have only three resistive analog sensor inputs supporting (LOP, FL, ET). (4-20mA current input should be removed) |
| 0.00 | 25 Jul 2017 | a. SRS taken From Kg645 R3, from that SRS below features are deleted 1. Main Monitoring 2. E-governing 3. MODBUS (RS485 Communication) 4. RTC 5. Expansion module 6. CAN which is used for expansion module 7. Cyclic Mode 8. DG Idle run features 9. MPU which is used for speed measurement 10 EEProm b. Hardware changes as per PCBP122 1. Analog sensor calculation formula change 2. Battery voltage calculation formula change 3. Charging alternator current calculation change |

1. Introduction and Nomenclature:

KG640 is a GCU developed especially for Kirloskar Oil Engine Limited (KOEL) by SEDEMAC. It is a sub-set of KG645 product. It is a modern and feature rich genset controllers with user-friendly HMI and full graphics LCD. The KG640 controllers come bundled with highly versatile software & extensive I/O's, and thereby support a wide variety of industry standard features in Petrol / diesel / gas / gasoline engine gensets. As a GCU (Generator Controller Unit), it will provide monitor and control for selected engine and alternator parameters. This product comprises of a GCU hardware, software and a by PC based configuration and flashing GUI utility.

For KG640 - detail SRS refer OHA SRS – PLM ID -SM0006695→SRS→ SED-OHA-SRS-SM0006695.

For KG640I - detail SRS refer OHA SRS – PLM ID - SM0010894→SRS→ SED-OHA-SRS-ISM0010894

# KG640 SRS has reference of KG645 SRS. The original SW SRS referred for this product: SEDMAC_GCU_SPECIFICATION.pdf in SRS folder of SM0001793

# This SRS is common for KG640 / KG640I. Following are the differences for the variant:

| # Sr No | # Product Name | # Features |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | # Alternator Voltage sensing | # Mains voltage sensing | # Load Sensing | # 4-20mA LOP sensor |
| # 1 | # KG640 | # Yes | # Yes | # Yes | # Yes |
| # 2 | # KG640I | # No | # No | # No | # Yes |

2. Requirement Trace-ability Matrix:  Only for new requirements which are different from KG645

| # | PRS section / sub-section ref | SW SRS ID |
| --- | --- | --- |
| 1 | Pin 23 should be used to measure mA output of 4-20mA Lube oil sensor. It should be called as channel S1. Pin 26 should be used for resistance type LOP measurement and it should be called channel S2. | FR-80 |
| 2 | Interlocking should be provided such that LOP measurement should not be available at channel S1 and channel S2 at the same time. | FR-81 |
| 3 | Pin 26 should be used to measure Lube Oil Temperature or Canopy Temperature when pin 23 is used is to measure LOP. For KG640I only: Pin25 should be used to measure LOT when pin26 is used for LOP | FR-82 |
| 4 | Digital Input I and its output should be added corresponding to the S2 channel. | FR-80 |
| 5 | Firmware should be compatible to bootloader GC1X-B04-R0V1 and to new hardware derived from PCB SM0010254. | FR-83, FR-84 |
| 6 | Remove RTC, MPU, CAN features from KG645-R4 features. Reserve expansion module parameters from MODBUS map. | FR-1 to FR-79 |
| 7 | Edge-triggered digital Input Semi-Auto mode should be added. | FR-45 |
| 8 | Information for maintenance, event log and other relevant features should be engine run hour based. | FR-13, FR-09 |
| 9 | KG640I – Remove Mains voltage sensing , Genset vtg sensing , load sensing. | FR03 |
| 10 | KG640I – Re-name Engine Temperature sensor to coolant temperature. Change range of Coolant temperature and LOT to -20 to 250 DegC. Change the open ckt action of LOT |  |

3. Requirements:

3.1 Functional Requirements:

| SW SRS ID | Description | PRS ID |
| --- | --- | --- |
| FR-01 | No Regional languages. Display only in English. | Verbal Form Sabu(KOEL) |
| FR-02 | Single Profile. | Verbal Form Sabu(KOEL) |
| FR-03 | Only for KG640: DG Phase rotation check. Add phase rotation alarm. Frequency, currents check for R, Y, B. No separate alarms for 3 phases. Volt check for R, Y, B separate alarms for 3 phases | SEDEMAC-GCU-Specification-Signoff: Generator Protection |
| FR-04 | KG640 -Temperature sensor range is -25 to200deg c KG640I – Rename Engine temperature sensor to Engine Coolant Temperature. Change range of all temperature sensor to -20 to 250degc. Similarly for warning and shutdown alarm ranges should be modified. | SEDEMAC-GCU-Specification: Temperature sensor details PRS ID 10 |
| FR-05 | Analog resistive inputs: 4 Nos. (3 Resistive and one 4-20ma). Following are the available sensors in combination (LOP, FL, ET, LOT, LOP4-20mA, Canopy Temp) Analog Sensor calculation change as per PCBP122A. For Fuel Reference: selection (Engine Body / Battery negative) added without GUI. Change analogue sensing formula as per PCBP123 & PCBP144. Remove fuel consumption parameter dependency over % Fuel display | SEDEMAC-GCU-Specification-Signoff: Analog Input Section |
| FR-06 | Logos only for the monitoring screens. No logos for the Alarms. As there is no EEprom, now logs are stored in internal EEprom. | Verbal Form Sabu(KOEL) |
| FR-07 | Only for KG640: When the speed (“Healthy Speed Threshold”) is not detected through the alternator frequency within 2 seconds after the engine starts, alarm should be generated as “Engine Speed Fault”. | SEDEMAC-GCU-Specification-Signoff: Generator Protection |
| FR-08 | Reserved |  |
| FR-09 | As no RTC available, Maintenance alarm will be configurable on Engine run hours. | KG640I SRS- 7. GUI/ UI parameters |
| FR-10 | KG640 only: Test mode as per EMS934 with Blink Indication on "Auto" and “Start” LED: Test mode will start with “Auto” long press. Will remain active till the test mode duration set in GCU is complete or will end when the “STOP” button is pressed. kG640I – Only Manual mode | KG640I: 6. Software Specifications: 3 |
| FR-11 | Number of starts counter (65000), No of trip counter (65000), For KG640 only KHW(5Million), KVAH(5Million). | SEDEMAC-GCU-Specification-Signoff: Specification- Counters |
| FR-12 | KOEL Logo at boot time duration of display to be fixed (4 sec). Product information screen followed by (5 sec) | SEDEMAC-GCU-Specification-Signoff: Specification-1-Boot up Screen |
| FR-13 | 30 event logs with Engine run hours stamping. | KG640I: 2. Requirements summary: software 2 |
| FR-14 | Only for KG640: Separate alarms for the 3 phases for low or high voltage. | SEDEMAC-GCU-Specification-Signoff: Generator Protection |
| FR-15 | Only for KG640: Load unbalance alarm: Alarm raised for Ph-Ph unbalance load for user defined threshold. | SEDEMAC-GCU-Specification-Signoff- Generator Protection |
| FR-16 | No governing |  |
| FR-17 | Status screen to pop up every time there is a change in the status. | Verbal Form Sabu (KOEL) |
| FR-18 | Only for KG640: CT coil calibration (+/- 1%, only through Laptop/GUI) | SEDEMAC-GCU-Specification-Signoff: Current Sensing |
| FR-19 | While coming out of the config mode, displays "saving settings". | Verbal Form Sabu(KOEL) |
| FR-20 | Over Speed trip with 2 levels: 1. Level1: Programmable RPM and delay, 2. Level2: %value above level1 speed should be programmable. Should be for fixed time delay(50-200ms) | SEDEMAC-GCU-Specification-Signoff: Over Speed Trip |
| FR-21 | Hour meter – Eng. Hours counted and displayed. | SEDEMAC-GCU-Specification-Signoff: Specification- Counters |
| FR-22 | Power saving mode: only LCD back light off | Verbal Form Sabu (KOEL) |
| FR-23 | For KG640: RPM reading through main alternator freq, no MPU for speed sensing. For KG640I: RPM measurement through MPU or w-point. | KG640I: 7. GUI/ UI parameters: 15 |
| FR-24 | Deep sleep mode implementation and safe recovery in all conditions. Current consumption not more than 12mA Configurable Digital Inputs:5 nos. | SEDEMAC-GCU-Specification-Signoff: Specification- Stand by Consumption |
| FR-25 | Configurable digital outputs: 6 Nos | SEDEMAC-GCU-Specification-Signoff: Digital Input Section |
| FR-26 | CHG Alternator output current: <=250mA rated. Change current calculation formula as per PCBP122. | SEDEMAC-GCU-Specification-Signoff: Charging Alt Fail input |
| FR-27 | No Expansion module, so no CAN |  |
| FR-28 | List of programmable timers: Crank time, crank rest time Safety monitoring start delay, alternator detect delay, crank start delay, engine cooling time, stop action time, load transfer delay, power save mode delay, screen changeover time, deep sleep mode delay Only for KG640I: Pull solenoid Timer | SEDEMAC-GCU-Specification-Signoff: Specification- List of Programmable Timers |
| FR-29 | Additional screen for displaying the contactor status | Verbal Form Sabu (KOEL) |
| FR-30 | Display "Cranking" with count down timer during crank time. Also display the "cool down", "stopping" with the countdown timer. | SEDEMAC-GCU-Specification-Signoff: Crank Disconnect logic |
| FR-31 | Additional configurable parameter "Fuel Liter Hr" which is used to calculate the remaining run hours for the current fuel. When this parameter is off, remaining hours are not displayed on the fuel screen. (This is configurable through GUI only). | Verbal Form Sabu (KOEL) |
| FR-32 | Only for KG640: Option for enabling and disabling the Phase rotation Shutdown. | Verbal Form Sabu (KOEL) |
| FR-33 | Separate parameter for the load transfer. If the transfer is configured as ON, only then the load is transferred on the DG. | Verbal Form Sabu (KOEL) |
| FR-34 | No start delay when preheat is configured in AUTO/MANUAL mode. | Verbal Form Sabu (KOEL) |
| FR-35 | Only for KG640: Additional configurable digital input source for the V belt broken switch. | Verbal Form Sabu (KOEL) |
| FR-36 | Minimum value of the battery voltage to be displayed in the battery voltage field. This value is the minimum battery voltage detected in run time. Change Battery voltage detection formula as per PCBP122A | Verbal From OHA (Vijay Patil) |
| FR-37 | MODBUS Communication over RS485. The MODBUS map should be compatible with KG645 R3. |  |
| FR-38 | Reserved |  |
| FR-39 | Audible alarm timer is configurable. It is named as Sounder Alarm. | Verbal Form Sabu (KOEL) |
| FR-40 | Displays "starting" during starting sequence. During starting sequence, it displays the countdown timer for Cranking, Warm up, run up and Idle up. Also displays the countdown timer for preheat. | SEDEMAC-GCU-Specification-Signoff: Crank Disconnect logic |
| FR-41 | Voltage reading should be with maximum 1% error. | SEDEMAC-GCU-Specification-Signoff: Generator Protection |
| FR-42 | Fuel theft alarm: to be generated when DG is OFF, GCU will enter the deep sleep mode if in Manual mode, should wake up every 1hr to check fuel theft. | Verbal Form Sabu (KOEL) |
| FR-43 | Only one “Stop action delay”. No “Additional stopping delay”. | Verbal Form Sabu (KOEL) |
| FR-44 | Remote Start/ Stop working same as Mains Unhealthy/Healthy, respectively. | Remote Start/ Stop |
| FR-45 | Edge triggered digital Input: Semi-Auto mode should be added. In manual mode if mains monitoring is enabled & in case mains is unhealthy, if Semi-Auto mode input is activated then DG should start. When DG voltage & frequency reaches healthy then genset contactor should be activated. When mains become healthy, DG should stop & GCU should go back in manual mode, transferring load on mains. If mains is healthy and Semi-Auto digital input is activated then controller should not start the DG. | SED-OHA-SRS-I-SM0001793 (R4)- Sr.No -4 |
| FR-46 | KG640 :Warning and shutdown actions should be available for Open Circuit alarms. KG640I: 4-20mA sensor open ckt should have shutdown/electrical trip alarms LOT sensor at number 25 should have open ckt alarm ( none/ warning/electrical trip/shutdown. | Verbal Form Sabu (KOEL) and PRS ID 10 |
| FR-47 | When “Emergency Stop” input received any time (Even when DG is OFF), GCU should start “Stopping” sequence. | Verbal Form Sabu (KOEL) |
| FR-48 | Charging alternator voltage-based crank disconnect should be present above configurable threshold. | SEDEMAC-GCU-Specification-Signoff: Charging Alternator I/O |
| FR-49 | All warnings should be auto cleared. | SEDEMAC-GCU-Specification-Signoff: Specification Charging Alternator I/o |
| FR-50 | Separate Warning and shutdown thresholds for Engine temperature sensor. | Verbal Form Sabu (KOEL) |
| FR-51 | Overload should have “Electrical Trip” as one of the actions, apart from Warning and shutdown. | SEDEMAC-GCU-Specification-Signoff: Generator Protection |
| FR-52 | Only for KG640: For DG frequency, GCU is displaying frequency of all 3 phases. There should not be any difference in these values, or it should display single frequency which will be minimum of all three frequencies. | Verbal Form Sabu (KOEL) |
| FR-53 | Only for KG640: Over current threshold should be in Ampere. | SEDEMAC-GCU-Specification-Signoff: Generator Protection |
| FR-54 | reserved |  |
| FR-55 | No Cyclic mode |  |
| FR-56 | No DG IDLE Run feature. |  |
| FR-57 | When any alarm Popped up, alarm screen will be displayed & GCU should hold that screen till manual key intervention. Alarm status is displayed over the MODBUS. | Verbal Form Sabu (KOEL) |
| FR-58 | Change memory map to make compatible with new boot loader & to avoid F/W check sum error. 1. Lock CFGC sector. 2. Save Password in CFGZ memory. 3. CFGZ check sum check added. | From OHA |
| FR-59 | GCU should support up to 25 digits alpha numeric character (allowed special characters are “.” “/”) engine serial number. Also, if number of digits are less than 25, it should display Sr. No. appropriately. | SEDEMAC-GCU-Specification-Signoff: Engine Serial Number tobe Displayed in information Screen SED-OHA-SRS-SM0001793-001(R4) – SR.No -3.09 |
| FR-60 | Fuel level to be displayed in Ltrs. Option should be enabled or disabled through config. | Verbal Form Sabu (KOEL) |
| FR-61 | Only for KG640: Take Overload rating in terms of KW not in KVA | SEDEMAC-GCU-Specification-Signoff: Generator Protection |
| FR-62 | Alarm screen should pop up even if the screen change over time is set to 0 | Verbal Form Sabu (KOEL) |
| FR-63 | For KG640: Batt volt, ph-ph voltages, KW, KVA, PF readings max 2% error. For KG640I: Batt volt readings max 2% error | SEDEMAC-GCU-Specification-Signoff: Specification – 7 & 8 |
| FR-64 | "OFF" mode implementation: After the TEST mode, go to OFF mode that do not allow to start the engine. To go to OFF mode press, STOP key in standby. To come out of OFF mode, press Manual/AUTO button to enter the valid mode. | SEDEMAC-GCU-Specification-Signoff:- Mode of Operation |
| FR-65 | Monitoring screens to be displayed in groups and should be able to jump to different groups using a key: use Up & Down keys (Both long press). | Verbal Form Sabu (KOEL) |
| FR-66 | Only for KG640: Per phase KW to be used for unbalanced detection. | SEDEMAC-GCU-Specification-Signoff- Generator Protection |
| FR-67 | For LOP provide level of warning & separate threshold for it. | SEDEMAC-GCU-Specification-Signoff: Analog Input |
| FR-68 | In Test Mode, all screens should have indication of test mode. | Verbal Form Sabu (KOEL) |
| FR-69 | STOP + DOWN key to go in config mode | Verbal Form Sabu (KOEL) |
| FR-70 | Reserved |  |
| FR-71 | STOP pressed for 3 sec to enter Boot loader mode while in “OFF mode” for connecting to PC- Smart Connect | Internal |
| FR-72 | Any key press to come out of Deep sleep mode | Verbal Form Sabu (KOEL) |
| FR-73 | Only for KG640: For “Alternator phase Voltage lost”, after crank disconnect, give 2sec delay or if the voltage is not built >=40/50v give the alarm. | SED-OHA-SRS-SM0001793-001 (R4)-Sr.No 4-B |
| FR-74 | Add new warnings, “Speed detected” & “Oil pressure detected” if its detected when the Start command is not through GCU & this is detected. | Verbal Form Sabu (KOEL) |
| FR-75 | Two password levels: Password level to be assigned to all parameters as per KOEL specs. | Verbal Form Sabu (KOEL) |
| FR-76 | Event to be logged for every config change. | Verbal Form Sabu (KOEL) |
| FR-77 | Reserved |  |
| FR-78 | Reserved |  |
| FR-79 | Reserved |  |
| FR-80 | Add support for Analog sensor S1- LOP 4-20mA type sensor (Pin 23) in the firmware. It can be used as Not Used/Digital Input I/Lube oil pressure. It should have separate low-level warning and shutdown thresholds. 10-point configurable look-up table of current (4-20mA) v/s pressure (0-10bar, resolution 0.1 bar) must be provided. | SEDEMAC-GCU-Specification-Signoff: Generator Protection |
| FR-81 | Interlocking must be provided between resistive LOP sensor and 4-20mA type LOP sensor selection. | Internal |
| FR-82 | Provision should be made to use sensor S2 (Pin 26) to measure Lube Oil Temperature and Canopy Temperature (Measurement Range: -25 degC to 200 degC) |  |
| FR-83 | Change memory map to make the firmware compatible to bootloader and smart flash. | Internal |
| FR-84 | Change charging alternator current calculation as per PCB derived from SM0010254. | Internal |
| FR-85 | Only for KG640: Digital Input Semi-Auto mode should be added: In manual mode if mains monitoring is enabled & in case of main unhealthy if Semi-Auto mode input is activated then DG should start. When DG voltage & frequency reaches healthy then genset contactor should be activated. When mains become healthy DG should stop & GCU should go back in manual mode, transferring load on mains. If mains healthy and Semi-Auto digital input is activated, then controller should not start the DG. Note: Digital input ‘Semi-Auto mode’ is edge triggered not continuous. | SED-OHA-SRS-ISM0006695- R1.00 |
| FR-86 | Only for KG640I: Pull Solenoid out Functionality: Pull solenoid is pulse type output, which should be turned on before cranking. Pull solenoid timing should be configurable. Also Turn on the Fuel relay in preheat state or in start delay. | KG640I: Details about Solenoid to be used with KG 640I |
| FR-87 | For KG640I only: Add Remote start functionality in Manual mode. |  |
| FR-88 | For KG640I only: Sperate ACK key in place of Auto key. |  |
| FR-89 | Add the parameter charging alternator voltage monitoring through battery. - If the parameter is enabled, then the controller should sense the battery voltage at the battery and take the actions as per configuration. - If the parameter is disabled, then the controller should sense the charging alternator voltage and take the actions as per configuration. | SED-OHA-SRS-C-SM0006695 |

3.2 Performance Requirements:

| SW SRS ID | Description | PRS ID |
| --- | --- | --- |

3.3 Interface Requirements:

| SW SRS ID | Description | PRS ID |
| --- | --- | --- |
| IR-01 | Keys to enter in “Auto mode” from manual mode and vice versa. | SEDEMAC-GCU-Specification-Signoff Mode of Operation |
| IR-02 | Keys for “Start” and “Stop” | SEDEMAC-GCU-Specification-Signoff Mode of Operation |
| IR-03 | For KG640: UP + DOWN to clear the alarm For KG640I: sperate ACK key in place of Auto mode | KG640I->SED-OHA-SRS-ISM0010894- Notes |
| IR-04 | USB: USB port as serial communication for firmware and config update. | SEDEMAC-GCU-Specification-Signoff Mode of Operation |
| IR-05 | RS485: 2W Half Duplex, 8 Bit, 1 stop bit, 1200, 4800, 9600, 57600, 13200, MODBUS: SEDEMAC protocol implemented. Please find MODBUS map in Doc folder of repository http://192.168.2.38:7990/projects/SW-GC1X/repos/kg640/browse/docs/Design/KG640I%20R1?at=refs%2Fheads%2Frelease%2FKG640I-R1-Demo-Code | SEDEMAC-GCU-Specification-Signoff- Communication |
| IR-06 | KOEL Smart Connect Application GUI should have following features. 1. Event log 2. Read / write parameters set. 3. Firmware flashing through Smart Flash. 4. Factory profile update through EOL | SEDEMAC-GCU-Specification-Signoff- Programming Tool |

3.4 Safety Requirements:

| SW SRS ID | Description | PRS ID |
| --- | --- | --- |
| SR-01 | Fuel theft logic as per KOEL spec: When DG is OFF, if the fuel level depletion rate (% as configured) will be more than the set value raise Fuel theft alarm. | Internal |
| SR-02 | 2 Levels of Password protections for parameters. Level 1: Access to critical parameters, Level 2: Full Access. The Password level of each parameter will be predefined. One password should be settable from GUI. | SEDEMAC-GCU-Specification-Signoff- Front Panel Editor Access |
| SR-03 | When Battery Voltage is less than 7.8v then do not write in internal EEPROM or in D-Flash memory (Configuration). This is to avoid the possibility corruption of Memory (F/W check sum error), which can stop device working. But when Device is USB powered then allow all memory operation. | Internal |
| SR-04 | Entering config mode shall not be possible while engine is running |  |

3.5 Other Requirements:

| SW SRS ID | Description | PRS ID |
| --- | --- | --- |

4. Not doing:

| # | PRS ID | Reason and / or justification for not meeting this requirement |
| --- | --- | --- |

5. Assumptions: None

| Prepared by: Name: Nikhil Mhaske Software Engineer 1-Oct-2021 | Reviewed by: Name: Madhuri Abhang Principal Engineer-SW 1-Oct-2021 | Approved by: Name: Pramod Ranade Chief Engineer - SW 1-Oct-2021 |
| --- | --- | --- |